## Lines
|  | Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
| Circuit name | Full name | Short name | Full name | Short name | Voltage level (kV) | Summer | Interseason 1 | Interseason 2 | Winter | DLRmin (A) | DLRmax (A) | Resistance R (Ω) | Reactance X (Ω) | Capacity (nF) | Half-Susceptance Hd/2 (μS) | Length (m)
AIRVAL61BONN6 | LIT 225kV N0 1 AIRVAULT-BONNEAU | AIRVAULT | AIRVA | BONNEAU | BONN6 | 225 | 932 | 932 | 1145 | 1145 |  |  | 3.064 | 20.35 | 762.736 | 119.81 | 52792
AIRVAL61JUMEA | LIT 225kV N0 1 AIRVAULT-JUMEAUX (LES) | AIRVAULT | AIRVA | JUMEAUX (LES) | JUMEA | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 0.33 | 2.212 | 50.501 | 7.933 | 5507
ALBERL61CHAV6 | LIT 225kV N0 1 ALBERTVILLE-CHAVANOD | ALBERTVILLE | ALBER | CHAVANOD | CHAV6 | 225 | 617 | 685 | 685 | 742 |  |  | 4.46 | 17.21 | 17.21 | 60 | 42135
ALBERL61CONTA | LIT 225kV N0 1 ALBERTVILLE-CONTAMINE | ALBERTVILLE | ALBER | CONTAMINE | CONTA | 225 | 565 | 673 | 673 | 765 |  |  | 2.352 | 10.043 | 225.097 | 35.358 | 24925
ALBERL61LONG6 | LIT 225kV N0 1 ALBERTVILLE-LONGEFAN | ALBERTVILLE | ALBER | LONGEFAN | LONG6 | 225 | 565 | 673 | 673 | 765 |  |  | 4.486 | 17.749 | 391.18 | 61.446 | 43669
ALBERL61MALGO | LIT 225kV N0 1 ALBERTVILLE-MALGOVERT | ALBERTVILLE | ALBER | MALGOVERT | MALGO | 225 | 565 | 673 | 673 | 765 |  |  | 3.54 | 16.64 | 363.641 | 55 | 40633
ALBERL61VEN.P | LIT 225kV N0 1 ALBERTVILLE-VENTHON-POSTE | ALBERTVILLE | ALBER | VENTHON-POSTE | VEN.P | 225 | 231 | 468 | 468 | 611 |  |  | 0.39 | 1.58 | 33.963 | 5 | 3790
ALLINL61CORNI | LIT 225kV N0 1 ALLINGES-CORNIER | ALLINGES | ALLIN | CORNIER | CORNI | 225 | 966 | 1076 | 1076 | 1168 |  |  | 2.42 | 14.488 | 343.724 | 53.992 | 36996
ANOULL61ETIVA | LIT 225kV N0 1 ANOULD-ETIVAL | ANOULD | ANOUL | ETIVAL | ETIVA | 225 | 1070 | 1155 | 1155 | 1265 |  |  | 2.888 | 19.202 | 433.075 | 68.027 | 47620
AOSTEL61BISSY | LIT 225kV N0 1 AOSTE-BISSY | AOSTE | AOSTE | BISSY | BISSY | 225 | 236 | 470 | 470 | 612 |  |  | 2.398 | 10.316 | 212.697 | 33.41 | 24490
AQUEDL61CIROL | LIT 225kV N0 1 AQUEDUCS (LES)-CIROLLIERS | AQUEDUCS (LES) | AQUED | CIROLLIERS | CIROL | 225 | 827 | 1015 | 1015 | 1150 |  |  | 0.549 | 3.644 | 84.418 | 13.26 | 9163
ARDOIL61MOTT5 | LIT 225kV N0 1 ARDOISE (L )-MOTTE (LA) (VILLENEUVE-LES-AVIGNON | ARDOISE (L ) | ARDOI | MOTTE (LA) (VILLENEUVE-LES-AVIGNON) | MOTT5 | 225 | 1025 | 1025 | 1200 | 1200 |  |  | 0.933 | 5.916 | 480.424 | 75.465 | 15768
ARDOIL61TAVEL | LIT 225kV N0 1 ARDOISE (L )-TAVEL | ARDOISE (L ) | ARDOI | TAVEL | TAVEL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.649 | 4.346 | 99.257 | 15.591 | 10819
ARENCL61B.MAI | LIT 225kV N0 1 ARENC-BELLE-DE-MAI | ARENC | ARENC | BELLE-DE-MAI | B.MAI | 225 | 510 | 510 | 640 | 640 |  |  | 0.251 | 0.483 | 447.275 | 70.258 | 2880
ARGIEL61ETUPE | LIT 225kV N0 1 ARGIESANS-ETUPES | ARGIESANS | ARGIE | ETUPES | ETUPE | 225 | 654 | 758 | 758 | 857 |  |  | 0.867 | 4.44 | 99.573 | 15.641 | 11145
ARGIEL61SIERE | LIT 225kV N0 1 ARGIESANS-SIERENTZ | ARGIESANS | ARGIE | SIERENTZ | SIERE | 225 | 654 | 758 | 758 | 857 |  |  | 4.645 | 21.857 | 483.444 | 75.939 | 54500
ARGOEL61B.CO6 | LIT 225kV N0 1 ARGOEUVES - BRAILLY-CORNEHOTTE | ARGOEUVES | ARGOE | BRAILLY-CORNEHOTTE | B.CO6 | 225 | 894 | 944 | 944 | 1017 |  |  | 3.497 | 15.821 | 347.289 | 54.552 | 38875
ARGOEL61BXCH5 | LIT 225kV N0 1 ARGOEUVES-BEAUCHAMPS | ARGOEUVES | ARGOE | BEAUCHAMPS | BXCH5 | 225 | 753 | 925 | 925 | 1075 |  |  | 3.214 | 21.636 | 493.648 | 77.542 | 54086
ARGOEL61BLOCA | LIT 225kV N0 1 ARGOEUVES-BLOCAUX | ARGOEUVES | ARGOE | BLOCAUX | BLOCA | 225 | 1250 | 1250 | 1250 | 1250 |  |  | 2.47 | 16.435 | 378.385 | 59.437 | 41056
ARLODL61GEN.P | LIT 225kV N0 1 ARLOD-GENISSIAT-POSTE | ARLOD | ARLOD | GENISSIAT-POSTE | GEN.P | 225 | 557 | 557 | 653 | 653 |  |  | 0.34 | 1.76 | 294.73 | 36 | 5279
ARNAGL61QUINT | LIT 225kV N0 1 ARNAGE-QUINTES (LES) | ARNAGE | ARNAG | QUINTES (LES) | QUINT | 225 | 1249 | 1316 | 1316 | 1389 |  |  | 0.336 | 2.231 | 51.678 | 8.118 | 5605
ARRIGL61CHEVI | LIT 225KV N0 1 ARRIGHI - CHEVILLY | ARRIGHI | ARRIG | CHEVILLY | CHEVI | 225 | 888 | 910 | 972 | 1049 |  |  | 0.962 | 5.29 | 536.591 | 84.287 | 14029
ARRIGL61CHARE | LIT 225kV N0 1 ARRIGHI-CHARENTON | ARRIGHI | ARRIG | CHARENTON | CHARE | 225 | 220 | 220 | 340 | 340 |  |  | 0.137 | 0.47 | 1300.111 | 204.221 | 4511
ARRIGL61MORBR | LIT 225kV N0 1 ARRIGHI-MORBRAS | ARRIGHI | ARRIG | MORBRAS | MORBR | 225 | 2008 | 2008 | 2300 | 2400 |  |  | 0.67 | 6.3 | 143.886 | 66.87 | 22138
ARRIGL61V.GEO | LIT 225kV N0 1 ARRIGHI-VILLENEUVE-ST-GEORGES | ARRIGHI | ARRIG | VILLENEUVE-ST-GEORGES | V.GEO | 225 | 750 | 750 | 830 | 830 |  |  | 0.42 | 2.62 | 1310.806 | 20.31 | 6719
ATTAQL61ECHIN | LIT 225kV N0 1 ATTAQUES (LES)-ECHINGHEN | ATTAQUES (LES) | ATTAQ | ECHINGHEN | ECHIN | 225 | 1002 | 1078 | 1078 | 1130 |  |  | 2.375 | 14.294 | 325.79 | 51.175 | 36192
ATTAQL61MANDA | LIT 225kV N0 1 ATTAQUES (LES)-MANDARINS | ATTAQUES (LES) | ATTAQ | MANDARINS | MANDA | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.607 | 4.047 | 93.155 | 14.633 | 10125
AUBE L61COMM7 | LIT 225kV N0 1 AUBE-COMMERVEIL | AUBE | AUBE | COMMERVEIL | COMM7 | 225 | 938 | 987 | 987 | 1041 |  |  | 4.993 | 22.672 | 484.664 | 76.131 | 54801
AUBE L61MEZE5 | LIT 225kV N0 1 AUBE-MEZEROLLES | AUBE | AUBE | MEZEROLLES | MEZE5 | 225 | 731 | 835 | 835 | 930 |  |  | 8.662 | 39.653 | 873.577 | 137.221 | 97448
AUBUSL61EGUZO | LIT 225kV N0 1 AUBUSSON-EGUZON | AUBUSSON | AUBUS | EGUZON | EGUZO | 225 | 894 | 991 | 991 | 1051 |  |  | 6.57 | 30.04 | 594.047 | 99 | 73228
AUBUSL61MOLE | LIT 225kV N0 1 AUBUSSON-MOLE (LA) | AUBUSSON | AUBUS |  | 1MOLE | 225 | 286 | 531 | 531 | 674 |  |  | 6.061 | 28.674 | 594.047 | 93.313 | 68298
AULNOL61P.SAM | LIT 225kV N0 1 AULNOYE-PONT-SUR-SAMBRE | AULNOYE | AULNO | PONT-SUR-SAMBRE | P.SAM | 225 | 975 | 1030 | 1030 | 1110 |  |  | 0.534 | 2.448 | 52.004 | 8.169 | 5897
AUSSOL61P.AND | LIT 225kV N0 1 AUSSOIS-PRAZ-ST-ANDRE | AUSSOIS | AUSSO | PRAZ-ST-ANDRE | P.AND | 225 | 737 | 820 | 820 | 889 |  |  | 1.07 | 4.33 | 93.222 | 15 | 10429
AUZATL61TARAS | LIT 225kV N0 1 AUZAT-TARASCON | AUZAT | AUZAT | TARASCON | TARAS | 225 | 737 | 820 | 820 | 889 |  |  | 1.64 | 6.387 | 141.615 | 22.245 | 15767
AVALLL61J.VIL | LIT 225kV N0 1 AVALLON - JOUX-LA-VILLE | AVALLON | AVALL | JOUX-LA-VILLE | J.VIL | 225 | 827 | 891 | 891 | 976 |  |  | 1.543 | 7.83 | 169.821 | 26.675 | 19039
AVELIL61MASTA | LIT 225kV N0 1 AVELIN - MASTAING | AVELIN | AVELI | MASTAING | MASTA | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.938 | 10.277 | 350.505 | 55.057 | 31508
AVELIL61CZRIE | LIT 225kV N0 1 AVELIN-COURRIERES | AVELIN | AVELI | COURRIERES | CZRIE | 225 | 1273 | 1346 | 1346 | 1451 |  |  | 1.086 | 7.461 | 174.65 | 27.434 | 18895
AVIGNL61CTAUR | LIT 225kV N0 1 AVIGNON (POSTE)-CHATEAURENARD | AVIGNON (POSTE) | AVIGN | CHATEAURENARD | CTAUR | 225 | 1198 | 1281 | 1281 | 1348 |  |  | 0.663 | 4.41 | 97.883 | 15.375 | 10858
AVIGNL61MOTT5 | LIT 225kV N0 1 AVIGNON (POSTE)-MOTTE (LA) (VILLENEUVE-LES-AVIG | AVIGNON (POSTE) | AVIGN | MOTTE (LA) (VILLENEUVE-LES-AVIGNON) | MOTT5 | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.355 | 2.363 | 54.376 | 8.541 | 5860
AVOINL61AVOI5 | LIT 225kV N0 1 AVOINE-AVOINE (POSTE 400 KV) | AVOINE | AVOIN | AVOINE (POSTE 400 KV) | AVOI5 | 225 | 1950 | 2025 | 2025 | 2100 |  |  | 0.042 | 0.275 | 295.206 | 46.371 | 1660
AVOINL61DISTR | LIT 225kV N0 1 AVOINE-DISTRE | AVOINE | AVOIN | DISTRE | DISTR | 225 | 915 | 915 | 1075 | 1075 |  |  | 1.294 | 8.775 | 505.343 | 79.379 | 23105
AVOINL61QUINT | LIT 225kV N0 1 AVOINE-QUINTES (LES) | AVOINE | AVOIN | QUINTES (LES) | QUINT | 225 | 1100 | 1186 | 1186 | 1275 |  |  | 4.462 | 30.705 | 722.018 | 113.414 | 78477
BACALL61BRUGE | LIT 225kV N0 1 BACALAN-BRUGES | BACALAN | BACAL | BRUGES | BRUGE | 225 | 655 | 655 | 760 | 760 |  |  | 0.593 | 3.97 | 104.383 | 16.397 | 9894
BACALL61MQIS | LIT 225kV N0 1 BACALAN-MARQUIS (LE) | BACALAN | BACAL |  | 1MQIS | 225 | 898 | 920 | 1030 | 1030 |  |  | 1.12 | 7.583 | 243.705 | 38.281 | 19408
BALARL61FLORE | LIT 225kV N0 1 BALARUC - FLORENSAC | BALARUC | BALAR | FLORENSAC | FLORE | 225 | 1161 | 1241 | 1241 | 1306 |  |  | 1.562 | 10.27 | 234.322 | 36.807 | 25565
BALARL61MTPEL | LIT 225kV N0 1 BALARUC - MONTPELLIER | BALARUC | BALAR | MONTPELLIER | MTPEL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.217 | 8.115 | 186.268 | 29.259 | 20281
BALMAL61VERFE | LIT 225kV N0 1 BALMA (POSTE)-VERFEIL | BALMA (POSTE) | BALMA | VERFEIL | VERFE | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 0.945 | 6.329 | 144.274 | 22.663 | 15743
BARBUL61CRENE | LIT 225kV N0 1 BARBUISE - CRENEY | BARBUISE | BARBU | CRENEY | CRENE | 225 | 684 | 781 | 781 | 869 |  |  | 5.296 | 24.684 | 521.343 | 81.892 | 59458
BARBUL61FOSSE | LIT 225kV N0 1 BARBUISE - FOSSES (LES) | BARBUISE | BARBU | FOSSES (LES) | FOSSE | 225 | 684 | 781 | 781 | 869 |  |  | 4.727 | 22.104 | 473.947 | 74.447 | 53523
BARJAL61CROI6 | LIT 225kV N0 1 BARJAC-CROISIERE | BARJAC | BARJA | CROISIERE | CROI6 | 225 | 660 | 694 | 694 | 756 |  |  | 4.819 | 15.387 | 377.728 | 59.333 | 38201
BASTIL61LANNE | LIT 225kV N0 1 BASTILLAC-LANNEMEZAN | BASTILLAC | BASTI | LANNEMEZAN | LANNE | 225 | 855 | 940 | 940 | 1025 |  |  | 3.166 | 20.675 | 471.514 | 74.065 | 51558
BATZEL61MARL6 | LIT 225kV N0 1 BATZENDORF-MARLENHEIM | BATZENDORF | BATZE | MARLENHEIM | MARL6 | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 1.804 | 11.989 | 277.055 | 43.52 | 29578
BAYETL61MTVIC | LIT 225kV N0 1 BAYET - MONTVICQ | BAYET | BAYET | MONTVICQ | MTVIC | 225 | 814 | 855 | 983 | 1000 |  |  | 2.11 | 14.64 | 389.314 | 59 | 37092
BAYETL61SEMIN | LIT 225kV N0 1 BAYET-SEMINAIRE | BAYET | BAYET | SEMINAIRE | SEMIN | 225 | 358 | 692 | 692 | 883 |  |  | 2.474 | 16.472 | 379.279 | 59.577 | 41254
BAYETL61VOLVI | LIT 225kV N0 1 BAYET-VOLVIC | BAYET | BAYET | VOLVIC | VOLVI | 225 | 814 | 983 | 983 | 1099 |  |  | 2.68 | 18.73 | 420.821 | 66 | 46358
BXLIEL61FARRA | LIT 225kV N0 1 BEAULIEU-FARRADIERE (LA) | BEAULIEU | BXLIE | FARRADIERE (LA) | FARRA | 225 | 632 | 890 | 890 | 1039 |  |  | 1.799 | 12.415 | 291.504 | 45.789 | 31532
BXLIEL61GRANZ | LIT 225kV N0 1 BEAULIEU-GRANZAY | BEAULIEU | BXLIE | GRANZAY | GRANZ | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 3.287 | 21.903 | 504.481 | 79.244 | 54903
BXLIEL61SIRMI | LIT 225kV N0 1 BEAULIEU-SIRMIERE | BEAULIEU | BXLIE | SIRMIERE | SIRMI | 225 | 1249 | 1337 | 1337 | 1432 |  |  | 4.007 | 27.335 | 639.524 | 100.456 | 69365
B.MONL61VALE8 | LIT 225kV N0 1 BEAUMONT-MONTEUX-VALENCE | BEAUMONT-MONTEUX | B.MON | VALENCE | VALE8 | 225 | 695 | 782 | 782 | 855 |  |  | 1.17 | 5.76 | 80.242 | 23 | 14022
BXRE6L61CHAIN | LIT 225kV N0 1 BEAUREGARD (SAINT-LAURENT-NOUAN)-CHAINGY | BEAUREGARD (SAINT-LAURENT-NOUAN) | BXRE6 | CHAINGY | CHAIN | 225 | 483 | 675 | 675 | 786 |  |  | 1.785 | 8.515 | 176.592 | 27.739 | 20498
BXTO5L61H.VIE | LIT 225kV N0 1 BEAUTOR (POSTE) - HERIE-LA-VIEVILLE | BEAUTOR (POSTE) | BXTO5 | HERIE-LA-VIEVILLE (LE) | H.VIE | 225 | 507 | 709 | 709 | 822 |  |  | 2.796 | 12.61 | 278.148 | 43.691 | 33458
BXTO5L61LATEN | LIT 225kV N0 1 BEAUTOR (POSTE)-LATENA | BEAUTOR (POSTE) | BXTO5 | LATENA | LATEN | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.75 | 12.011 | 282.326 | 44.348 | 30447
BXTO5L61L.CHA | LIT 225kV N0 1 BEAUTOR (POSTE)-LONG-CHAMP (LE) | BEAUTOR (POSTE) | BXTO5 | LONG-CHAMP (LE) | L.CHA | 225 | 731 | 835 | 835 | 930 |  |  | 4.258 | 20.966 | 463.941 | 72.876 | 51911
BXTO5L61SETIE | LIT 225kV N0 1 BEAUTOR (POSTE)-SETIER | BEAUTOR (POSTE) | BXTO5 | SETIER | SETIE | 225 | 899 | 984 | 984 | 1061 |  |  | 1.916 | 8.609 | 190.318 | 29.895 | 21161
B.MAIL61E.BOT | LIT 225kV N0 1 BELLE-DE-MAI-ENCO-DE-BOTTE | BELLE-DE-MAI | B.MAI | ENCO-DE-BOTTE | E.BOT | 225 | 610 | 610 | 705 | 705 |  |  | 0.266 | 1.759 | 1888.299 | 296.613 | 10280
B.EPIL61DOMLO | LIT 225kV N0 1 BELLE-EPINE - DOMLOUP | BELLE-EPINE | B.EPI | DOMLOUP | DOMLO | 225 | 934 | 934 | 1154 | 1154 |  |  | 1.018 | 6.863 | 480.841 | 75.53 | 18083
B.EPIL61RAN.P | LIT 225kV N0 1 BELLE-EPINE-RANCE-POSTE | BELLE-EPINE | B.EPI | RANCE-POSTE | RAN.P | 225 | 795 | 864 | 864 | 931 |  |  | 6.323 | 28.584 | 630.79 | 99.084 | 70250
BERG9L61CANTE | LIT 225kV N0 1 BERGE - CANTEGRIT | BERGE | BERG9 | CANTEGRIT | CANTE | 225 | 915 | 985 | 985 | 1060 |  |  | 1.22 | 7.945 | 184.077 | 28.915 | 19966
BERG9L61MARSI | LIT 225kV N0 1 BERGE - MARSILLON | BERGE | BERG9 | MARSILLON | MARSI | 225 | 915 | 985 | 985 | 1060 |  |  | 3.479 | 22.666 | 525.045 | 82.474 | 57047
BERGHL61MARL6 | LIT 225kV N0 1 BERGHOLZ-MARLENHEIM | BERGHOLZ | BERGH | MARLENHEIM | MARL6 | 225 | 2200 | 2281 | 2281 | 2281 |  |  | 0.767 | 11.003 | 548.769 | 86.2 | 41359
BEZAUL61C.MET | LIT 225kV N0 1 BEZAUMONT-CROIX-DE-METZ | BEZAUMONT | BEZAU | CROIX-DE-METZ | C.MET | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.571 | 10.705 | 250.849 | 39.403 | 27115
BEZAUL61CUSTI | LIT 225kV N0 1 BEZAUMONT-CUSTINE | BEZAUMONT | BEZAU | CUSTINE | CUSTI | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.761 | 5.07 | 116.626 | 18.32 | 12619
BEZAUL61VANDI | LIT 225kV N0 1 BEZAUMONT-VANDIERES | BEZAUMONT | BEZAU | VANDIERES | VANDI | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.819 | 5.445 | 125.596 | 19.728 | 13646
BEZ.EL61SSVIN | LIT 225KV N0 1 BEZIERS-EST - ST-VINCENT | BEZIERS-EST | BEZ.E | ST-VINCENT | SSVIN | 225 | [6 empty] | 0.259 | 0.761 | 729.029 | 114.516 | 4443
BEZONL61PTCHA | LIT 225kV N0 1 BEZON-PONTCHATEAU | BEZON | BEZON | PONTCHATEAU | PTCHA | 225 | 846 | 928 | 928 | 1005 |  |  | 6.782 | 35.208 | 791.752 | 124.368 | 86496
BEZONL61P.ROU | LIT 225kV N0 1 BEZON-POTEAU ROUGE | BEZON | BEZON | POTEAU-ROUGE | P.ROU | 225 | 983 | 1022 | 1022 | 1059 |  |  | 6.829 | 35.619 | 800.523 | 125.746 | 88449
BIANCL61FREJU | LIT 225kV N0 1 BIANCON - FREJUS | BIANCON | BIANC | FREJUS | FREJU | 225 | 1100 | 1100 | 1600 | 1600 |  |  | 0.402 | 4.098 | 7161.972 | 1125 | 24588
BIANCL61MOUGI | LIT 225kV N0 1 BIANCON-MOUGINS | BIANCON | BIANC | MOUGINS | MOUGI | 225 | 1000 | 1000 | 1160 | 1185 |  |  | 0.987 | 5.296 | 2065.384 | 324.43 | 18456
BIANCL61P.GR5 | LIT 225kV N0 1 BIANCON-PLAN-DE-GRASSE | BIANCON | BIANC | PLAN-DE-GRASSE | P.GR5 | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.705 | 5.149 | 1680.571 | 263.983 | 17853
BISSYL61G.ILE | LIT 225kV N0 1 BISSY-GRANDE-ILE | BISSY | BISSY | GRANDE-ILE | G.ILE | 225 | 566 | 672 | 672 | 764 |  |  | 1.63 | 7.68 | 339.624 | 53.348 | 18962
BLOCAL61LIMEU | LIT 225kV N0 1 BLOCAUX - LIMEUX (400 kV) | BLOCAUX | BLOCA | LIMEUX | LIMEU | 225 | 967 | 967 | 1218 | 1218 |  |  | 0.72 | 5.423 | 6012.937 | 944.51 | 29137
BOISSL61CUS.P | LIT 225kV N0 1 BOISSE (LA) - CUSSET-POSTE | BOISSE (LA) | BOISS | CUSSET-POSTE | CUS.P | 225 | 857 | 857 | 1024 | 1024 |  |  | 0.66 | 4.98 | 231.834 | 37 | 12613
BOISSL61GEN.P | LIT 225kV N0 1 BOISSE (LA) - GENISSIAT-POSTE | BOISSE (LA) | BOISS | GENISSIAT-POSTE | GEN.P | 225 | 695 | 725 | 782 | 855 |  |  | 6.206 | 27.41 | 664.814 | 104.429 | 68301
BOISSL61SSV.E | LIT 225kV N0 1 BOISSE (LA) - ST-VULBAS-EST | BOISSE (LA) | BOISS | ST-VULBAS-EST | SSV.E | 225 | 900 | 1015 | 1015 | 1112 |  |  | 1.263 | 8.463 | 193.12 | 30.335 | 21057
BOLL5L61C.RHO | LIT 225kV N0 1 BOLLENE-CHATEAUNEUF-DU-RHONE | BOLLENE (POSTE RESEAU) | BOLL5 | CHATEAUNEUF-DU-RHONE | C.RHO | 225 | 816 | 889 | 889 | 947 |  |  | 1.996 | 10.196 | 321.471 | 50.496 | 24939
BOLL5L61TERRA | LIT 225kV N0 1 BOLLENE-TERRADOU | BOLLENE (POSTE RESEAU) | BOLL5 | TERRADOU | TERRA | 225 | 816 | 889 | 889 | 947 |  |  | 3.767 | 17.664 | 391.633 | 61.518 | 43937
BOLL5L61TRI.P | LIT 225kV N0 1 BOLLENE-TRICASTIN-POSTE (LE) | BOLLENE (POSTE RESEAU) | BOLL5 | TRICASTIN-POSTE (LE) | TRI.P | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.325 | 2.172 | 49.607 | 7.792 | 5560
BONN6L61ORANG | LIT 225kV N0 1 BONNEAU-ORANGERIE (L) | BONNEAU | BONN6 | ORANGERIE (L) | ORANG | 225 | 1012 | 1150 | 1150 | 1247 |  |  | 2.124 | 14.107 | 326.062 | 51.218 | 35413
BONN6L61VALDI | LIT 225kV N0 1 BONNEAU-VALDIVIENNE | BONNEAU | BONN6 | VALDIVIENNE | VALDI | 225 | 1180 | 1310 | 1310 | 1390 |  |  | 1.656 | 10.454 | 269.701 | 42.365 | 27611
BONNIL61MEZE5 | LIT 225kV N0 1 BONNIERES - MEZEROLLES | BONNIERES | BONNI | MEZEROLLES | MEZE5 | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.702 | 11.349 | 260.899 | 40.982 | 28492
BOUDEL61C.RHO | LIT 225kV N0 1 BOUDEYRE-CHATEAUNEUF-DU-RHONE | BOUDEYRE | BOUDE | CHATEAUNEUF-DU-RHONE | C.RHO | 225 | 862 | 928 | 928 | 987 |  |  | 2.433 | 11.463 | 254.689 | 40.006 | 28383
BOUDEL61MTPEZ | LIT 225kV N0 1 BOUDEYRE-MONTPEZAT | BOUDEYRE | BOUDE | MONTPEZAT | MTPEZ | 225 | 862 | 928 | 928 | 987 |  |  | 1.724 | 7.671 | 170.081 | 26.716 | 19100
BOULEL61PUTEA | LIT 225kV N0 1 BOULE (LA) - PUTEAUX | BOULE (LA) | BOULE | PUTEAUX | PUTEA | 225 | 490 | 490 | 730 | 730 |  |  | 0.091 | 0.613 | 909.857 | 142.92 | 3507
BZGUIL61ETUPE | LIT 225kV N0 1 BOURGUIGNON - ETUPES | BOURGUIGNON | BZGUI | ETUPES | ETUPE | 225 | 791 | 853 | 853 | 934 |  |  | 1.431 | 5.598 | 123.897 | 19.462 | 13832
BZGUIL61MAMBE | LIT 225kV N0 1 BOURGUIGNON - MAMBELIN | BOURGUIGNON | BZGUI | MAMBELIN | MAMBE | 225 | 791 | 853 | 853 | 934 |  |  | 1.143 | 4.789 | 107.252 | 16.847 | 11881
BOUTRL61TRANS | LIT 225kV N0 1 BOUTRE - TRANS | BOUTRE | BOUTR | TRANS | TRANS | 225 | 1250 | 1250 | 1600 | 1600 |  |  | 1.02 | 10.4 | 15603.551 | 2451 | 64661
BOUTRL61COUDO | LIT 225kV N0 1 BOUTRE-COUDON (LE) | BOUTRE | BOUTR | COUDON (LE) | COUDO | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 1.641 | 17.352 | 837.968 | 131.628 | 63400
BOUTRL61SSTUL | LIT 225kV N0 1 BOUTRE-SAINTE-TULLE 1 | BOUTRE | BOUTR | STE-TULLE | SSTUL | 225 | 1144 | 1249 | 1249 | 1333 |  |  | 0.705 | 5.573 | 118.414 | 18.6 | 13295
B.CO6L61SORRU | LIT 225kV N0 1 BRAILLY-CORNEHOTTE - SORRUS | BRAILLY-CORNEHOTTE | B.CO6 | SORRUS | SORRU | 225 | 865 | 865 | 865 | 865 |  |  | 2.769 | 12.603 | 278.064 | 43.678 | 30947
BRENNL61MARTY | LIT 225kV N0 1 BRENNILIS-MARTYRE (LA) | BRENNILIS | BRENN | MARTYRE (LA) | MARTY | 225 | 1250 | 1312 | 1312 | 1375 |  |  | 1.762 | 12.128 | 284.449 | 44.681 | 31072
BRENNL61P.CHR | LIT 225kV N0 1 BRENNILIS-PLEYBER-CHRIST | BRENNILIS | BRENN | PLEYBER-CHRIST | P.CHR | 225 | 1300 | 1350 | 1350 | 1400 |  |  | 1.297 | 8.601 | 199.244 | 31.297 | 21445
BREN5L61PELIS | LIT 225kV N0 1 BRENS - PELISSIER | BRENS (CNR) | BREN5 | PELISSIER | PELIS | 225 | 831 | 984 | 984 | 1099 |  |  | 0.979 | 6.546 | 151.199 | 23.75 | 16576
BREN5L61VERFE | LIT 225kV N0 1 BRENS - VERFEIL | BRENS (CNR) | BREN5 | VERFEIL | VERFE | 225 | 831 | 984 | 984 | 1099 |  |  | 2.35 | 15.638 | 360.313 | 56.598 | 39187
BREUIL61ZSSG7 | LIT 225kV N0 1 BREUIL (LE) - PIQUAGE A SAINT GERONS | BREUIL (LE) | BREUI |  | ZSSG7 | 225 | 629 | 756 | 756 | 844 |  |  | 3.063 | 13.853 | 304.349 | 47.807 | 34393
BREUIL61MOLE | LIT 225kV N0 1 BREUIL (LE)-MOLE (LA) | BREUIL (LE) | BREUI |  | 1MOLE | 225 | 622 | 748 | 748 | 834 |  |  | 1.791 | 8.345 | 173.528 | 27.258 | 19922
BREUIL61P.CHA | LIT 225kV N0 1 BREUIL (LE)-PEYRAT-LE-CHATEAU | BREUIL (LE) | BREUI | PEYRAT-LE-CHATEAU | P.CHA | 225 | 629 | 756 | 756 | 844 |  |  | 6.396 | 28.64 | 634.473 | 99.663 | 71580
B.CARL61LINGO | LIT 225kV N0 1 BROC-CARROS (LE) - LINGOSTIERE | BROC-CARROS (LE) | B.CAR | LINGOSTIERE | LINGO | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.69 | 4.616 | 105.429 | 16.561 | 11971
B.CARL61T.VIC | LIT 225kV N0 1 BROC-CARROS (LE) - TRINITE-VICTOR | BROC-CARROS (LE) | B.CAR | TRINITE-VICTOR | T.VIC | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.812 | 5.476 | 128.204 | 20.263 | 13853
BRODEL61ZDUV5 | LIT 225kV N0 1 BRODE - PIQUAGE A DUVIGNEAU | BRODE | BRODE | PIQUAGE A DUVIGNEAU | ZDUV5 | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.023 | 0.155 | 3.532 | 0.555 | 368
BRUGEL61PESSA | LIT 225kV N0 1 BRUGES-PESSAC | BRUGES | BRUGE | PESSAC | PESSA | 225 | 655 | 655 | 760 | 760 |  |  | 0.828 | 5.538 | 135.568 | 21.295 | 13884
BUIREL61P.SAM | LIT 225kV N0 1 BUIRE-PONT-SUR-SAMBRE | BUIRE | BUIRE | PONT-SUR-SAMBRE | P.SAM | 225 | 1250 | 1250 | 1250 | 1250 |  |  | 2.641 | 17.72 | 402.398 | 63.208 | 44040
B.CHAL61ROMAI | LIT 225kV N0 1 BUTTES-CHAUMONT-ROMAINVILLE | BUTTES-CHAUMONT | B.CHA | ROMAINVILLE | ROMAI | 225 | 440 | 440 | 550 | 550 |  |  | 0.17 | 0.66 | 1828.054 | 287 | 6198
CAEN L61RANVI | LIT 225kV N0 1 CAEN - RANVILLE | CAEN | CAEN | RANVILLE | RANVI | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.45 | 3.021 | 67.955 | 10.674 | 7494
CALA5L61P.ROU | LIT 225kV N0 1 CALAN - POTEAU-ROUGE | CALAN | CALA5 | POTEAU-ROUGE | P.ROU | 225 | 1110 | 1110 | 1403 | 1403 |  |  | 0.104 | 1.067 | 1620.028 | 254.473 | 6800
CANTEL61MARSI | LIT 225kV N0 1 CANTEGRIT-MARSILLON | CANTEGRIT | CANTE | MARSILLON | MARSI | 225 | 997 | 1096 | 1096 | 1155 |  |  | 4.678 | 30.486 | 706.69 | 111.007 | 77402
CANTEL61MOUGU | LIT 225kV N0 1 CANTEGRIT-MOUGUERRE | CANTEGRIT | CANTE | MOUGUERRE | MOUGU | 225 | 1884 | 1890 | 1890 | 1890 |  |  | 4.563 | 33.778 | 749.573 | 117.743 | 83100
CANTEL61NAOUT | LIT 225kV N0 1 CANTEGRIT-NAOUTOT | CANTEGRIT | CANTE | NAOUTOT | NAOUT | 225 | 935 | 1000 | 1000 | 1080 |  |  | 2.296 | 15.425 | 346.771 | 54.471 | 38208
CAPELL61H.VIE | LIT 225kV N0 1 CAPELLE (LA) - HERIE-LA-VIEVILLE | CAPELLE (LA) | CAPEL | HERIE-LA-VIEVILLE (LE) | H.VIE | 225 | 579 | 709 | 709 | 822 |  |  | 2.985 | 14.747 | 328.979 | 51.676 | 33829
CAPELL61P.SAM | LIT 225kV N0 1 CAPELLE (LA)-PONT-SUR-SAMBRE | CAPELLE (LA) | CAPEL | PONT-SUR-SAMBRE | P.SAM | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 1.827 | 12.238 | 278.731 | 43.783 | 30470
CARRIL61P.GAS | LIT 225kV N0 1 CARRIERES - PLESSIS-GASSOT | CARRIERES | CARRI | PLESSIS-GASSOT | P.GAS | 225 | 510 | 767 | 767 | 976 |  |  | 1.622 | 10.781 | 243.979 | 38.324 | 26831
CARRIL61VALES | LIT 225KV N0 1 CARRIERES - VALESCOURT | CARRIERES | CARRI | VALESCOURT | VALES | 225 | [6 empty] | 2.065 | 13.764 | 315.97 | 49.632 | 34429
CARRIL61MORU | LIT 225kV N0 1 CARRIERES-MORU | CARRIERES | CARRI |  | 1MORU | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.7 | 11.31 | 263.745 | 40.71 | 28277
CARRIL61TERRI | LIT 225kV N0 1 CARRIERES-TERRIER | CARRIERES | CARRI | TERRIER | TERRI | 225 | 2046 | 2300 | 2300 | 2400 |  |  | 0.469 | 4.417 | 202.596 | 31.824 | 15649
CSLL8L61SAUMA | LIT 225kV N0 1 CASTELLE (LA) - SAUMADE | CASTELLE (LA) | CSLL8 | SAUMADE | SAUMA | 225 | 745 | 775 | 932 | 940 |  |  | 0.49 | 3.271 | 487.114 | 76.516 | 9379
CSLL8L61TAMAR | LIT 225kV N0 1 CASTELLE (LA) - TAMAREAU | CASTELLE (LA) | CSLL8 | TAMAREAU | TAMAR | 225 | 745 | 870 | 932 | 1010 |  |  | 1.455 | 9.013 | 232.525 | 36.525 | 27295
CSLLEL61E.BOT | LIT 225kV N0 1 CASTELLET (LE) - ENCO-DE-BOTTE | CASTELLET (LE) | CSLLE | ENCO-DE-BOTTE | E.BOT | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.344 | 8.918 | 206.602 | 32.453 | 22408
CSLLEL61ESCAI | LIT 225kV N0 1 CASTELLET (LE) - ESCAILLON (L ) | CASTELLET (LE) | CSLLE | ESCAILLON (L ) | ESCAI | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.199 | 7.95 | 184.179 | 28.931 | 19976
CAZARL61JALIS | LIT 225kV N0 1 CAZARIL-JALIS | CAZARIL | CAZAR | JALIS | JALIS | 225 | 828 | 908 | 908 | 986 |  |  | 6.635 | 33.492 | 753.608 | 118.377 | 83146
CAZARL61LANNE | LIT 225kV N0 1 CAZARIL-LANNEMEZAN | CAZARIL | CAZAR | LANNEMEZAN | LANNE | 225 | 828 | 908 | 908 | 986 |  |  | 1.054 | 5.037 | 105.481 | 16.569 | 12123
CERGYL61P.GAS | LIT 225kV N0 1 CERGY - PLESSIS-GASSOT | CERGY | CERGY | PLESSIS-GASSOT | P.GAS | 225 | 520 | 782 | 782 | 998 |  |  | 1.982 | 17.165 | 397.818 | 62.489 | 43020
CERGYL61PORCH | LIT 225kV N0 1 CERGY-PORCHEVILLE | CERGY | CERGY | PORCHEVILLE | PORCH | 225 | 926 | 1060 | 1060 | 1181 |  |  | 1.632 | 10.7 | 246.587 | 38.734 | 27066
CERGYL61PUISE | LIT 225kV N0 1 CERGY-PUISEUX | CERGY | CERGY | PUISEUX | PUISE | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.28 | 1.865 | 42.995 | 6.754 | 4670
CERNAL61VESLE | LIT 225kV N0 1 CERNAY-VESLE | CERNAY | CERNA | VESLE | VESLE | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.051 | 7.006 | 161.138 | 25.311 | 17550
CESTAL61MASQU | LIT 225kV N0 1 CESTAS - MASQUET | CESTAS | CESTA | MASQUET | MASQU | 225 | 932 | 1049 | 1049 | 1126 |  |  | 1.049 | 6.969 | 201.756 | 31.692 | 17600
CESTAL61PESSA | LIT 225kV N0 1 CESTAS - PESSAC | CESTAS | CESTA | PESSAC | PESSA | 225 | 932 | 1049 | 1049 | 1126 |  |  | 0.842 | 5.602 | 176.514 | 27.727 | 14472
CHABOL61CHEV5 | LIT 225kV N0 1 CHABOSSIERE (LA)-CHEVIRE | CHABOSSIERE (LA) | CHABO | CHEVIRE | CHEV5 | 225 | 1249 | 1337 | 1337 | 1432 |  |  | 0.422 | 2.86 | 67.157 | 10.549 | 7334
CHABOL61COR.P | LIT 225kV N0 1 CHABOSSIERE (LA)-CORDEMAIS-POSTE | CHABOSSIERE (LA) | CHABO | CORDEMAIS-POSTE | COR.P | 225 | 1249 | 1337 | 1337 | 1432 |  |  | 1.114 | 7.536 | 177.749 | 27.921 | 19522
CHAINL61DAMBR | LIT 225kV N0 1 CHAINGY-DAMBRON | CHAINGY | CHAIN | DAMBRON | DAMBR | 225 | 888 | 983 | 983 | 1042 |  |  | 1.572 | 10.561 | 237.417 | 37.293 | 26338
CHALOL61CPVAN | LIT 225kV N0 1 CHALON-CHAMPVANS | CHALON | CHALO | CHAMPVANS | CPVAN | 225 | 641 | 742 | 742 | 836 |  |  | 5.585 | 25.536 | 548.76 | 86.199 | 61860
CHALOL61GROSN | LIT 225kV N0 1 CHALON-GROSNE | CHALON | CHALO | GROSNE | GROSN | 225 | 1400 | 1500 | 1500 | 1550 |  |  | 0.752 | 7.047 | 327.043 | 51.372 | 25080
CPNIEL61EYBEN | LIT 225kV N0 1 CHAMPAGNIER-EYBENS | CHAMPAGNIER | CPNIE | EYBENS | EYBEN | 225 | 1093 | 1178 | 1178 | 1253 |  |  | 0.519 | 3.384 | 78.195 | 12.283 | 8400
CPNIEL61GRISO | LIT 225kV N0 1 CHAMPAGNIER-GRISOLLES | CHAMPAGNIER | CPNIE | GRISOLLES | GRISO | 225 | 734 | 856 | 856 | 964 |  |  | 5.011 | 32.529 | 832.447 | 130.76 | 82181
CPNIEL61MOIRA | LIT 225kV N0 1 CHAMPAGNIER-MOIRANS | CHAMPAGNIER | CPNIE | MOIRANS | MOIRA | 225 | 1123 | 1211 | 1211 | 1290 |  |  | 1.075 | 11.551 | 405.294 | 63.663 | 35406
CPNIEL61PARIS | LIT 225kV N0 1 CHAMPAGNIER-PARISET | CHAMPAGNIER | CPNIE | PARISET | PARIS | 225 | 570 | 659 | 659 | 739 |  |  | 1.13 | 3.95 | 94.024 | 14 | 9410
CPNIEL61S.PON | LIT 225kV N0 1 CHAMPAGNIER-SERRE-PONCON | CHAMPAGNIER | CPNIE | SERRE-PONCON | S.PON | 225 | 734 | 856 | 856 | 964 |  |  | 5.92 | 39.82 | 982.981 | 150 | 98635
CPNOLL61FRASN | LIT 225kV N0 1 CHAMPAGNOLE - FRASNE | CHAMPAGNOLE | CPNOL | FRASNE | FRASN | 225 | 801 | 930 | 930 | 1053 |  |  | 1.637 | 9.735 | 230.251 | 36.168 | 24838
CPNOLL61SAONE | LIT 225kV N0 1 CHAMPAGNOLE - SAONE | CHAMPAGNOLE | CPNOL | SAONE | SAONE | 225 | 455 | 555 | 555 | 632 |  |  | 7.144 | 24.248 | 484.608 | 76.122 | 56775
CPNOLL61GEN.P | LIT 225kV N0 1 CHAMPAGNOLE-GENISSIAT-POSTE | CHAMPAGNOLE | CPNOL | GENISSIAT-POSTE | GEN.P | 225 | 264 | 437 | 437 | 545 |  |  | 11.011 | 36.498 | 725.184 | 113.912 | 85139
C.REGL61VIELM | LIT 225kV N0 1 CHAMPS-REGNAUD-VIELMOULIN | CHAMPS-REGNAUD | C.REG | VIELMOULIN | VIELM | 225 | 843 | 909 | 909 | 996 |  |  | 2.649 | 12.359 | 273.779 | 43.005 | 30500
CPVANL61PYMON | LIT 225kV N0 1 CHAMPVANS-PYMONT | CHAMPVANS | CPVAN | PYMONT | PYMON | 225 | 751 | 923 | 923 | 1056 |  |  | 2.767 | 19.099 | 448.426 | 70.439 | 48515
C.GOML61E.BOT | LIT 225kV N0 1 CHATEAU-GOMBERT - ENCO-DE-BOTTE | CHATEAU-GOMBERT | C.GOM | ENCO-DE-BOTTE | E.BOT | 225 | 438 | 438 | 438 | 438 |  |  | 0.337 | 1.122 | 1092.959 | 171.682 | 6355
C.RHOL61TRI.P | LIT 225kV N0 1 CHATEAUNEUF-DU-RHONE - TRICASTIN-POSTE (LE) | CHATEAUNEUF-DU-RHONE | C.RHO | TRICASTIN-POSTE (LE) | TRI.P | 225 | 862 | 928 | 928 | 987 |  |  | 1.723 | 8.881 | 196.801 | 30.913 | 21904
C.RHOL61L.NEU | LIT 225kV N0 1 CHATEAUNEUF-DU-RHONE-LOGIS-NEUF | CHATEAUNEUF-DU-RHONE | C.RHO | LOGIS-NEUF | L.NEU | 225 | 862 | 928 | 928 | 987 |  |  | 2.693 | 12.205 | 266.346 | 41.838 | 30000
CXSSEL61RECY | LIT 225kV N0 1 CHAUSSEE (LA)-RECY | CHAUSSEE (LA) | CXSSE |  | 1RECY | 225 | 1172 | 1268 | 1268 | 1355 |  |  | 1.598 | 10.643 | 236.404 | 37.134 | 26238
CXSSEL61REVIG | LIT 225kV N0 1 CHAUSSEE (LA)-REVIGNY | CHAUSSEE (LA) | CXSSE | REVIGNY | REVIG | 225 | 1140 | 1248 | 1248 | 1347 |  |  | 2.335 | 15.545 | 342.603 | 53.816 | 38162
CHAV6L61GEN.P | LIT 225kV N0 1 CHAVANOD-GENISSIAT-POSTE | CHAVANOD | CHAV6 | GENISSIAT-POSTE | GEN.P | 225 | 617 | 659 | 685 | 742 |  |  | 4.69 | 16.11 | 379.272 | 56 | 39113
CHESNL61CZTRY | LIT 225kV N0 1 CHESNOY (LE)-COURTRY | CHESNOY (LE) | CHESN | COURTRY | CZTRY | 225 | 899 | 984 | 984 | 1061 |  |  | 1.747 | 8.063 | 179.581 | 28.208 | 19948
CHESNL61NEMOU | LIT 225kV N0 1 CHESNOY (LE)-NEMOURS | CHESNOY (LE) | CHESN | NEMOURS | NEMOU | 225 | 520 | 782 | 782 | 998 |  |  | 2.114 | 14.347 | 337.116 | 52.954 | 36369
CHESNL61ROUSS | LIT 225kV N0 1 CHESNOY (LE)-ROUSSON | CHESNOY (LE) | CHESN | ROUSSON | ROUSS | 225 | 786 | 867 | 867 | 948 |  |  | 4.082 | 18.523 | 569.01 | 89.38 | 45817
CHEVIL61V.GEO | LIT 225KV N0 1 CHEVILLY - VILLENEUVE-ST- | CHEVILLY | CHEVI | VILLENEUVE-ST-GEORGES | V.GEO | 225 | 750 | 750 | 830 | 830 |  |  | 0.63 | 3.118 | 94.156 | 14.79 | 7503
CHEVIL61CORIO | LIT 225kV N0 1 CHEVILLY-CORIOLIS | CHEVILLY | CHEVI | CORIOLIS | CORIO | 225 | 425 | 425 | 540 | 540 |  |  | 0.556 | 1.326 | 2313.906 | 363.467 | 10695
CHEV5L61MERLA | LIT 225kV N0 1 CHEVIRE-MERLATIERE | CHEVIRE | CHEV5 | MERLATIERE | MERLA | 225 | 1249 | 1337 | 1337 | 1432 |  |  | 2.997 | 20.647 | 483.815 | 75.998 | 52396
CHEV5L61VERTO | LIT 225kV N0 1 CHEVIRE-VERTOU | CHEVIRE | CHEV5 | VERTOU | VERTO | 225 | 706 | 821 | 821 | 911 |  |  | 1.074 | 4.891 | 105.352 | 16.549 | 11895
CHOLEL61MAUGE | LIT 225kV N0 1 CHOLET - MAUGES (LES) | CHOLET | CHOLE | MAUGES (LES) | MAUGE | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 1.565 | 10.41 | 239.935 | 37.689 | 25072
CHOLEL61DISTR | LIT 225kV N0 1 CHOLET-DISTRE | CHOLET | CHOLE | DISTRE | DISTR | 225 | 915 | 915 | 1075 | 1075 |  |  | 3.953 | 26.547 | 640.054 | 100.54 | 66007
CHOLEL61V.SEV | LIT 225kV N0 1 CHOLET-VAL-DE-SEVRE | CHOLET | CHOLE | VAL-DE-SEVRE | V.SEV | 225 | 803 | 858 | 858 | 918 |  |  | 4.502 | 16.299 | 338.407 | 53.157 | 38688
CHOO5L61MAZUR | LIT 225kV N0 1 CHOOZ-MAZURES | CHOOZ | CHOO5 | MAZURES | MAZUR | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 0.852 | 8.755 | 366.925 | 57.637 | 29393
CIROLL61LOGES | LIT 225kV N0 1 CIROLLIERS - LOGES (LES) | CIROLLIERS | CIROL | LOGES (LES) | LOGES | 225 | 880 | 880 | 1130 | 1130 |  |  | 0.4 | 2.709 | 225.201 | 35.374 | 7205
CISSAL61MQIS | LIT 225kV N0 1 CISSAC-MARQUIS (LE) | CISSAC | CISSA |  | 1MQIS | 225 | 1172 | 1248 | 1248 | 1310 |  |  | 2.285 | 15.118 | 1048.103 | 108.21 | 39310
CIZE L61FLEYR | LIT 225kV N0 1 CIZE-FLEYRIAT | CIZE | CIZE | FLEYRIAT | FLEYR | 225 | 1059 | 1067 | 1141 | 1212 |  |  | 1.216 | 7.669 | 365.614 | 57.431 | 24233
CIZE L61IZERN | LIT 225kV N0 1 CIZE-IZERNORE | CIZE | CIZE | IZERNORE | IZERN | 225 | 1059 | 1141 | 1141 | 1215 |  |  | 0.454 | 2.701 | 63.791 | 10.02 | 6970
CLEONL61G.COU | LIT 225kV N0 1 CLEON-GRAND-COURONNE | CLEON | CLEON | GRAND-COURONNE | G.COU | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.328 | 2.197 | 50.137 | 7.876 | 5470
CLEONL61MANOI | LIT 225kV N0 1 CLEON-MANOIR (LE) | CLEON | CLEON | MANOIR (LE) | MANOI | 225 | 1270 | 1366 | 1366 | 1433 |  |  | 0.88 | 5.92 | 131.692 | 21 | 14651
COLAYL61DONZA | LIT 225kV N0 1 COLAYRAC-DONZAC | COLAYRAC | COLAY | DONZAC | DONZA | 225 | 831 | 984 | 984 | 1099 |  |  | 1.756 | 11.772 | 266.109 | 41.8 | 29278
COLAYL61GUPIE | LIT 225kV N0 1 COLAYRAC-GUPIE | COLAYRAC | COLAY | GUPIE | GUPIE | 225 | 895 | 980 | 980 | 1070 |  |  | 3.214 | 21.383 | 492.659 | 77.387 | 53496
COMM7L61CPFL5 | LIT 225kV N0 1 COMMERVEIL-CHAMPFLEUR | COMMERVEIL | COMM7 | CHAMPFLEUR | CPFL5 | 225 | 1249 | 1316 | 1316 | 1389 |  |  | 1.317 | 8.75 | 202.308 | 31.778 | 21943
COMPIL61LATEN | LIT 225kV N0 1 COMPIEGNE-LATENA | COMPIEGNE | COMPI | LATENA | LATEN | 225 | 881 | 964 | 964 | 1040 |  |  | 3.041 | 14.566 | 314.924 | 49.468 | 35410
COMPIL61MORU | LIT 225kV N0 1 COMPIEGNE-MORU | COMPIEGNE | COMPI |  | 1MORU | 225 | 716 | 817 | 817 | 910 |  |  | 1.82 | 8.91 | 191.276 | 29.45 | 21472
CONCAL61P.ROU | LIT 225kV N0 1 CONCARNEAU - POTEAU-ROUGE | CONCARNEAU | CONCA | POTEAU-ROUGE | P.ROU | 225 | 1056 | 1123 | 1123 | 1189 |  |  | 3.245 | 22.203 | 519.984 | 81.679 | 56304
CONCAL61SQUIV | LIT 225kV N0 1 CONCARNEAU-SQUIVIDAN | CONCARNEAU | CONCA | SQUIVIDAN | SQUIV | 225 | 1056 | 1123 | 1123 | 1189 |  |  | 1.516 | 10.244 | 238.911 | 37.528 | 26103
CONF5L61CPNIE | LIT 225kV N0 1 CONFLUENT-CHAMPAGNIER | CONFLUENT | CONF5 | CHAMPAGNIER | CPNIE | 225 | 618 | 718 | 718 | 800 |  |  | 1.76 | 9.15 | 238.911 | 30 | 22412
CONF5L61PARIS | LIT 225kV N0 1 CONFLUENT-PARISET | CONFLUENT | CONF5 | PARISET | PARIS | 225 | 850 | 850 | 1078 | 1078 |  |  | 0.12 | 0.78 | 63.736 | 9 | 2045
CONTAL61G.COE | LIT 225kV N0 1 CONTAMINE-GRAND-COEUR | CONTAMINE | CONTA | GRAND-COEUR | G.COE | 225 | 966 | 1076 | 1076 | 1168 |  |  | 0.548 | 3.245 | 77.19 | 12.125 | 8384
CONTAL61MALGO | LIT 225kV N0 1 CONTAMINE-MALGOVERT | CONTAMINE | CONTA | MALGOVERT | MALGO | 225 | 565 | 673 | 673 | 765 |  |  | 2.26 | 10.86 | 248.076 | 38 | 27527
COQUAL61DRONN | LIT 225kV N0 1 COQUAINVILLIERS-DRONNIERE (LA) | COQUAINVILLIERS | COQUA | DRONNIERE (LA) | DRONN | 225 | 955 | 955 | 1130 | 1130 |  |  | 2.484 | 16.711 | 439.497 | 69.036 | 41564
COQUAL61ROUGE | LIT 225kV N0 1 COQUAINVILLIERS-ROUGEMONTIER | COQUAINVILLIERS | COQUA | ROUGEMONTIER | ROUGE | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 2.797 | 18.835 | 424.314 | 66.651 | 46232
COQUAL61TOURB | LIT 225kV N0 1 COQUAINVILLIERS-TOURBE | COQUAINVILLIERS | COQUA | TOURBE | TOURB | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 2.212 | 14.928 | 334.257 | 52.505 | 36875
CORBIL61DISTR | LIT 225kV N0 1 CORBIERE (LA)-DISTRE | CORBIERE (LA) | CORBI | DISTRE | DISTR | 225 | 1213 | 1298 | 1298 | 1375 |  |  | 2.766 | 18.428 | 406.02 | 63.777 | 45457
COR.PL61ZPLUV | LIT 225kV N0 1 CORDEMAIS-POSTE - PIQUAGE A BASTILLE | CORDEMAIS-POSTE | COR.P | PIQUAGE A PLUVIGNER | ZPLUV | 225 | 1175 | 1258 | 1258 | 1347 |  |  | 1.079 | 7.31 | 172.608 | 27.113 | 19931
COR.PL61PTCHA | LIT 225kV N0 1 CORDEMAIS-POSTE-PONTCHATEAU | CORDEMAIS-POSTE | COR.P | PONTCHATEAU | PTCHA | 225 | 829 | 909 | 909 | 984 |  |  | 2.524 | 12.411 | 276.888 | 43.493 | 30704
CORNIL61PRESS | LIT 225kV N0 1 CORNIER-PRESSY | CORNIER | CORNI | PRESSY | PRESS | 225 | 966 | 1076 | 1076 | 1168 |  |  | 1.453 | 8.965 | 211.43 | 33.211 | 22797
COSSIL61MORBR | LIT 225kV N0 1 COSSIGNY-MORBRAS | COSSIGNY | COSSI | MORBRAS | MORBR | 225 | 888 | 972 | 972 | 1049 |  |  | 0.516 | 2.482 | 55.201 | 8.671 | 6135
COUCHL61CPVAN | LIT 225kV N0 1 COUCHEY-CHAMPVANS | COUCHEY | COUCH | CHAMPVANS | CPVAN | 225 | 847 | 985 | 985 | 1116 |  |  | 2.388 | 15.865 | 366.499 | 57.57 | 39710
COUCHL61VIELM | LIT 225kV N0 1 COUCHEY-VIELMOULIN | COUCHEY | COUCH | VIELMOULIN | VIELM | 225 | 800 | 900 | 900 | 1000 |  |  | 1.798 | 11.941 | 276.063 | 43.364 | 29900
COUDOL61NEOUL | LIT 225kV N0 1 COUDON (LE) - NEOULES | COUDON (LE) | COUDO | NEOULES | NEOUL | 225 | 1001 | 1093 | 1093 | 1165 |  |  | 1.094 | 6.574 | 153.038 | 24.039 | 16595
COUDOL61ESCAI | LIT 225kV N0 1 COUDON (LE)-ESCAILLON (L ) | COUDON (LE) | COUDO | ESCAILLON (L ) | ESCAI | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.786 | 5.258 | 122.768 | 19.284 | 13200
CZTRYL61SENAR | LIT 225kV N0 1 COURTRY-SENART | COURTRY | CZTRY | SENART | SENAR | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.073 | 7.207 | 306.908 | 48.209 | 18326
CREC6L61WEPPE | LIT 225kV N0 1 CRECHETS (LES) - WEPPES | CRECHETS (LES) | CREC6 | WEPPES | WEPPE | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.876 | 5.842 | 134.397 | 21.111 | 14607
CREC6L61GUARB | LIT 225kV N0 1 CRECHETS (LES)-GUARBECQUE | CRECHETS (LES) | CREC6 | GUARBECQUE | GUARB | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.43 | 9.5 | 219.744 | 34.517 | 23478
CRENEL61FRONC | LIT 225kV N0 1 CRENEY - FRONCLES | CRENEY | CRENE | FRONCLES | FRONC | 225 | 899 | 984 | 984 | 1061 |  |  | 6.818 | 34.112 | 765.294 | 120.212 | 84751
CRENEL61ROSIE | LIT 225kV N0 1 CRENEY-ROSIERES | CRENEY | CRENE | ROSIERES | ROSIE | 225 | 899 | 984 | 984 | 1061 |  |  | 2.31 | 12.393 | 267.514 | 42.021 | 30108
CRETAL61TOLBI | LIT 225kV N0 1 CRETAINE-TOLBIAC | CRETAINE | CRETA | TOLBIAC | TOLBI | 225 | 620 | 620 | 690 | 690 |  |  | 0.16 | 0.48 | 771.125 | 108 | 4386
C.METL61LANEU | LIT 225kV N0 1 CROIX-DE-METZ-LANEUVEVILLE | CROIX-DE-METZ | C.MET | LANEUVEVILLE | LANEU | 225 | 899 | 984 | 984 | 1061 |  |  | 2.836 | 15.641 | 355.868 | 55.9 | 39040
C.METL61VOID | LIT 225kV N0 1 CROIX-DE-METZ-VOID | CROIX-DE-METZ | C.MET |  | 1VOID | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.931 | 12.851 | 296.38 | 46.555 | 32175
CUBNEL61GREZI | LIT 225kV N0 1 CUBNEZAIS-GREZILLAC | CUBNEZAIS | CUBNE | GREZILLAC | GREZI | 225 | 932 | 1049 | 1049 | 1126 |  |  | 1.983 | 13.287 | 314.292 | 49.369 | 34160
CUBNEL61MQIS | LIT 225kV N0 1 CUBNEZAIS-MARQUIS (LE) | CUBNEZAIS | CUBNE |  | 1MQIS | 225 | 1748 | 2048 | 2048 | 2222 |  |  | 0.359 | 3.488 | 140.309 | 22.04 | 11884
CUBNEL61MTGUY | LIT 225kV N0 1 CUBNEZAIS-MONTGUYON | CUBNEZAIS | CUBNE | MONTGUYON | MTGUY | 225 | 951 | 1104 | 1104 | 1170 |  |  | 2.529 | 14.39 | 344.285 | 54.08 | 36716
CUBNEL61TUILI | LIT 225kV N0 1 CUBNEZAIS-TUILIERES | CUBNEZAIS | CUBNE | TUILIERES | TUILI | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 3.867 | 26.093 | 1440.235 | 226.232 | 95931
DAMERL61NOGEN | LIT 225kV N0 1 DAMERY-NOGENTEL | DAMERY | DAMER | NOGENTEL | NOGEN | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 2.257 | 15.015 | 346.158 | 54.374 | 37720
DAMERL61VESLE | LIT 225kV N0 1 DAMERY-VESLE | DAMERY | DAMER | VESLE | VESLE | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 2.612 | 17.457 | 400.139 | 62.854 | 43188
DANTOL61TUILI | LIT 225kV N0 1 DANTOU-TUILIERES | DANTOU | DANTO | TUILIERES | TUILI | 225 | 642 | 757 | 757 | 845 |  |  | 4.112 | 18.659 | 411.717 | 64.672 | 45976
DANTOL61VERLH | LIT 225kV N0 1 DANTOU-VERLHAGUET | DANTOU | DANTO | VERLHAGUET | VERLH | 225 | 289 | 543 | 543 | 682 |  |  | 5.605 | 25.282 | 557.367 | 87.551 | 66225
DARSEL61FEUIL | LIT 225kV N0 1 DARSE - FEUILLANE | DARSE | DARSE | FEUILLANE | FEUIL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.787 | 5.273 | 120.211 | 18.883 | 13143
DARSEL61RASSU | LIT 225kV N0 1 DARSE-RASSUEN | DARSE | DARSE | RASSUEN | RASSU | 225 | 795 | 795 | 970 | 970 |  |  | 1.028 | 6.364 | 689.503 | 108.307 | 17682
DECHYL61GAVRE | LIT 225kV N0 1 DECHY - GAVRELLE | DECHY | DECHY | GAVRELLE | GAVRE | 225 | 975 | 1030 | 1030 | 1110 |  |  | 2.42 | 12.124 | 314.091 | 49.337 | 30663
DECHYL61MASTA | LIT 225kV N0 1 DECHY-MASTAING | DECHY | DECHY | MASTAING | MASTA | 225 | 935 | 1000 | 1000 | 1080 |  |  | 1.705 | 18.414 | 172.721 | 27.131 | 19226
D.FRAL61LINGO | LIT 225kV N0 1 DIGUE-DES-FRANCAIS-LINGOSTIERE | DIGUE-DES-FRANCAIS | D.FRA | LINGOSTIERE | LINGO | 225 | 708 | 708 | 847 | 847 |  |  | 0.308 | 2.045 | 593.925 | 93.294 | 6540
DISTRL61MONDI | LIT 225kV N0 1 DISTRE - MONDION | DISTRE | DISTR | MONDION | MONDI | 225 | 957 | 1023 | 1023 | 1096 |  |  | 4.824 | 21.992 | 485.594 | 76.277 | 53588
DOBERL61RAN.P | LIT 225kV N0 1 DOBERIE - RANCE-POSTE | DOBERIE | DOBER | RANCE-POSTE | RAN.P | 225 | 1104 | 1222 | 1222 | 1315 |  |  | 2.133 | 14.721 | 345.412 | 54.257 | 37272
DOBERL61TREGU | LIT 225kV N0 1 DOBERIE - TREGUEUX | DOBERIE | DOBER | TREGUEUX | TREGU | 225 | 1217 | 1266 | 1266 | 1322 |  |  | 1.421 | 9.807 | 230.339 | 36.182 | 24854
DONZAL61VERLH | LIT 225kV N0 1 DONZAC-VERLHAGUET | DONZAC | DONZA | VERLHAGUET | VERLH | 225 | 831 | 960 | 984 | 1099 |  |  | 2.644 | 17.552 | 477.782 | 75.05 | 44328
DONZEL61FEROU | LIT 225kV N0 1 DONZENAC-FEROUGE | DONZENAC | DONZE | FEROUGE | FEROU | 225 | 814 | 983 | 983 | 1099 |  |  | 2.58 | 17.133 | 396.48 | 62.279 | 43009
DRONNL61TOURB | LIT 225kV N0 1 DRONNIERE (LA) - TOURBE | DRONNIERE (LA) | DRONN | TOURBE | TOURB | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.614 | 4.094 | 94.202 | 14.797 | 10567
DRONNL61FLERS | LIT 225kV N0 1 DRONNIERE (LA)-FLERS | DRONNIERE (LA) | DRONN | FLERS | FLERS | 225 | 1250 | 1312 | 1312 | 1375 |  |  | 2.977 | 20.563 | 482.663 | 75.817 | 52330
DUVIGL61ZDUV5 | LIT 225kV N0 1 DUVIGNEAU - PIQUAGE A DUVIGNEAU | DUVIGNEAU | DUVIG | PIQUAGE A DUVIGNEAU | ZDUV5 | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.018 | 0.116 | 2.692 | 0.423 | 292
ECHALL61GIVOR | LIT 225kV N0 1 ECHALAS - GIVORS | ECHALAS | ECHAL | GIVORS | GIVOR | 225 | 900 | 910 | 1015 | 1080 |  |  | 0.42 | 2.89 | 118.61 | 18 | 6946
ECHALL61RIVIE | LIT 225kV N0 1 ECHALAS-RIVIERE (LA) | ECHALAS | ECHAL | RIVIERE (LA) | RIVIE | 225 | 1800 | 2030 | 2030 | 2224 |  |  | 0.865 | 8.422 | 363.397 | 57.082 | 28844
ECHALL61SOLEI | LIT 225kV N0 1 ECHALAS-SOLEIL (LE) | ECHALAS | ECHAL | SOLEIL (LE) | SOLEI | 225 | 1375 | 1437 | 1437 | 1500 |  |  | 0.89 | 8.83 | 263.939 | 54 | 28207
ECHINL61MANDA | LIT 225kV N0 1 ECHINGHEN-MANDARINS | ECHINGHEN | ECHIN | MANDARINS | MANDA | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.919 | 12.79 | 294.186 | 46.211 | 31993
ECHINL61SORRU | LIT 225kV N0 1 ECHINGHEN-SORRUS | ECHINGHEN | ECHIN | SORRUS | SORRU | 225 | 935 | 935 | 935 | 935 |  |  | 2.65 | 12.047 | 265.956 | 41.776 | 29715
EGUZOL61MARMA | LIT 225kV N0 1 EGUZON-MARMAGNE | EGUZON | EGUZO | MARMAGNE | MARMA | 225 | 274 | 412 | 412 | 476 |  |  | 14.456 | 40.726 | 827.989 | 130.06 | 92576
EGUZOL61MAURE | LIT 225kV N0 1 EGUZON-MAUREIX (LE) | EGUZON | EGUZO | MAUREIX (LE) | MAURE | 225 | 905 | 1003 | 1003 | 1063 |  |  | 6.387 | 30.781 | 688.857 | 108.205 | 76254
EGUZOL61MTLUC | LIT 225kV N0 1 EGUZON-MONTLUCON | EGUZON | EGUZO | MONTLUCON | MTLUC | 225 | 497 | 596 | 596 | 663 |  |  | 10.43 | 34.48 | 665.417 | 107 | 79482
EGUZOL61MOUS5 | LIT 225kV N0 1 EGUZON-MOUSSEAUX | EGUZON | EGUZO | MOUSSEAUX | MOUS5 | 225 | 520 | 831 | 831 | 895 |  |  | 4.591 | 21.708 | 541.339 | 85.033 | 51013
EGUZOL61ORANG | LIT 225kV N0 1 EGUZON-ORANGERIE (L) | EGUZON | EGUZO | ORANGERIE (L) | ORANG | 225 | 409 | 644 | 644 | 761 |  |  | 8.454 | 38.123 | 840.902 | 132.089 | 94599
EGUZOL61SSFEY | LIT 225kV N0 1 EGUZON-STE-FEYRE | EGUZON | EGUZO | STE-FEYRE | SSFEY | 225 | 832 | 921 | 921 | 975 |  |  | 3.918 | 16.521 | 382.808 | 60.131 | 41628
ELANCL61MEZE5 | LIT 225kV N0 1 ELANCOURT-MEZEROLLES | ELANCOURT | ELANC | MEZEROLLES | MEZE5 | 225 | 1140 | 1248 | 1248 | 1347 |  |  | 1.676 | 10.871 | 254.538 | 39.983 | 27540
ELANCL61SSAU5 | LIT 225kV N0 1 ELANCOURT-ST-AUBIN | ELANCOURT | ELANC | ST-AUBIN | SSAU5 | 225 | 511 | 768 | 768 | 979 |  |  | 1.122 | 7.373 | 187.354 | 29.429 | 18556
ELANCL61YVE.O | LIT 225kV N0 1 ELANCOURT-YVELINES-OUEST | ELANCOURT | ELANC | YVELINES-OUEST | YVE.O | 225 | 1056 | 1056 | 1360 | 1360 |  |  | 0.298 | 2.013 | 2990.108 | 469.685 | 12751
E.BOTL61RABAT | LIT 225kV N0 1 ENCO-DE-BOTTE - RABATAU | ENCO-DE-BOTTE | E.BOT | RABATAU | RABAT | 225 | 400 | 400 | 715 | 715 |  |  | 0.713 | 4.3 | 1475.909 | 231.835 | 14103
E.BOTL61REALT | LIT 225kV N0 1 ENCO-DE-BOTTE - REALTOR | ENCO-DE-BOTTE | E.BOT | REALTOR | REALT | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.336 | 8.918 | 204.274 | 32.087 | 23562
E.BOTL61PALUN | LIT 225kV N0 1 ENCO-DE-BOTTE-PALUN (LA) | ENCO-DE-BOTTE | E.BOT | PALUN (LA) | PALUN | 225 | 1001 | 1093 | 1093 | 1165 |  |  | 1.12 | 7.113 | 164.034 | 25.447 | 17835
ENVALL61ISSOI | LIT 225kV N0 1 ENVAL-ISSOIRE | ENVAL | ENVAL | ISSOIRE | ISSOI | 225 | 617 | 740 | 740 | 826 |  |  | 2.87 | 13.21 | 274.535 | 47 | 31568
ENVALL61VOLVI | LIT 225kV N0 1 ENVAL-VOLVIC | ENVAL | ENVAL | VOLVIC | VOLVI | 225 | 814 | 983 | 983 | 1099 |  |  | 0.87 | 6.07 | 137.014 | 21 | 15031
ESCAIL61NEOUL | LIT 225kV N0 1 ESCAILLON (L ) - NEOULES | ESCAILLON (L ) | ESCAI | NEOULES | NEOUL | 225 | 935 | 935 | 1085 | 1085 |  |  | 0.956 | 7.044 | 2531.642 | 397.669 | 24415
FALLOL61NOVIO | LIT 225kV N0 1 FALLOU-NOVION | FALLOU | FALLO | NOVION | NOVIO | 225 | 620 | 620 | 690 | 690 |  |  | 0.157 | 0.536 | 1484.903 | 233.248 | 4998
FAMARL61G.CAI | LIT 225kV N0 1 FAMARS-GROS-CAILLOU | FAMARS | FAMAR | GROS-CAILLOU | G.CAI | 225 | 975 | 1030 | 1030 | 1110 |  |  | 1.407 | 6.986 | 156.509 | 24.584 | 17235
FARRAL61SAINT | LIT 225kV N0 1 FARRADIERE (LA) - SAINTES | FARRADIERE (LA) | FARRA | SAINTES | SAINT | 225 | 1180 | 1310 | 1310 | 1390 |  |  | 1.912 | 12.791 | 383.505 | 60.241 | 32262
FARRAL61GRANZ | LIT 225kV N0 1 FARRADIERE (LA)-GRANZAY | FARRADIERE (LA) | FARRA | GRANZAY | GRANZ | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 2.551 | 17.077 | 389.208 | 61.137 | 43118
FEROUL61TALAM | LIT 225kV N0 1 FEROUGE-TALAMET | FEROUGE | FEROU | TALAMET | TALAM | 225 | 895 | 980 | 980 | 1070 |  |  | 2.487 | 16.515 | 382.162 | 60.03 | 41489
FEUILL61PONTE | LIT 225kV N0 1 FEUILLANE - PONTEAU | FEUILLANE | FEUIL | PONTEAU | PONTE | 225 | 1375 | 1437 | 1437 | 1500 |  |  | 0.554 | 5.84 | 226.84 | 35.632 | 19037
FEUILL61LAVER | LIT 225kV N0 1 FEUILLANE-LAVERA | FEUILLANE | FEUIL | LAVERA | LAVER | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.021 | 6.858 | 154.998 | 24.347 | 17020
FEUILL61SSCHA | LIT 225kV N0 1 FEUILLANE-ST-CHAMAS | FEUILLANE | FEUIL | ST-CHAMAS | SSCHA | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 2.041 | 13.924 | 324.42 | 50.96 | 35580
FLANDL61ROMAI | LIT 225kV N0 1 FLANDRE - ROMAINVILLE | FLANDRE | FLAND | ROMAINVILLE | ROMAI | 225 | 633 | 633 | 738 | 738 |  |  | 0.16 | 0.64 | 914.364 | 140 | 5295
FLEACL61MQIS | LIT 225kV N0 1 FLEAC-MARQUIS (LE) | FLEAC | FLEAC |  | 1MQIS | 225 | 1112 | 1233 | 1233 | 1307 |  |  | 5.538 | 36.782 | 848.116 | 133.222 | 92259
FLEACL61MTGUY | LIT 225kV N0 1 FLEAC-MONTGUYON | FLEAC | FLEAC | MONTGUYON | MTGUY | 225 | 831 | 921 | 921 | 975 |  |  | 7.482 | 26.459 | 523.504 | 82.232 | 62460
FLEACL61NIORT | LIT 225kV N0 1 FLEAC-NIORT | FLEAC | FLEAC | NIORT | NIORT | 225 | 524 | 644 | 644 | 717 |  |  | 10.395 | 37.201 | 737.938 | 115.915 | 86837
FLEACL61SANIL | LIT 225kV N0 1 FLEAC-SANILHAC | FLEAC | FLEAC | SANILHAC | SANIL | 225 | 642 | 757 | 757 | 845 |  |  | 8.058 | 36.644 | 803.787 | 126.259 | 90158
FLERSL61LAUNA | LIT 225kV N0 1 FLERS-LAUNAY | FLERS | FLERS | LAUNAY | LAUNA | 225 | 539 | 675 | 675 | 781 |  |  | 5.018 | 22.63 | 1144.305 | 179.747 | 57880
FLEYRL61VOUGL | LIT 225kV N0 1 FLEYRIAT-VOUGLANS | FLEYRIAT | FLEYR | VOUGLANS | VOUGL | 225 | 850 | 959 | 959 | 1050 |  |  | 2.82 | 17.02 | 389.777 | 62 | 42068
FLOIRL61MQIS | LIT 225kV N0 1 FLOIRAC-MARQUIS (LE) | FLOIRAC | FLOIR |  | 1MQIS | 225 | 929 | 965 | 1088 | 1140 |  |  | 1.506 | 9.859 | 316.919 | 49.781 | 24720
FLOIRL61PESSA | LIT 225kV N0 1 FLOIRAC-PESSAC | FLOIRAC | FLOIR | PESSAC | PESSA | 225 | 932 | 1049 | 1049 | 1126 |  |  | 1.347 | 9.018 | 205.977 | 32.355 | 22465
FLOREL61SSVIN | LIT 225kV N0 1 FLORENSAC - ST VINCENT | FLORENSAC | FLORE | ST-VINCENT | SSVIN | 225 | 1161 | 1241 | 1241 | 1306 |  |  | 1.705 | 10.144 | 239.771 | 37.663 | 25831
FONT L61RIORG | LIT 225kV N0 1 FONT (LA)-RIORGES | FONT (LA) | FONT | RIORGES | RIORG | 225 | 358 | 692 | 692 | 883 |  |  | 3.015 | 20.203 | 467.102 | 73.372 | 50746
FOUSCL61TAMAR | LIT 225kV N0 1 FOUSCAIS - TAMAREAU | FOUSCAIS | FOUSC | TAMAREAU | TAMAR | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.495 | 10.017 | 228.364 | 35.871 | 24931
FREJUL61TRANS | LIT 225kV N0 1 FREJUS-TRANS | FREJUS | FREJU | TRANS | TRANS | 225 | 1062 | 1066 | 1160 | 1238 |  |  | 1.383 | 9.223 | 301.747 | 47.398 | 22800
GAMPAL61P.EVE | LIT 225kV N0 1 GAMPALOUP - PONT-EVEQUE | GAMPALOUP | GAMPA | PONT-EVEQUE | P.EVE | 225 | 880 | 992 | 992 | 1086 |  |  | 1.43 | 9.66 | 226.212 | 34 | 24656
GANGEL61SSVIC | LIT 225kV N0 1 GANGES - ST VICTOR | GANGES | GANGE | ST-VICTOR | SSVIC | 225 | 325 | 457 | 457 | 572 |  |  | 10.901 | 30.969 | 702.048 | 110.277 | 77078
GANGEL61VIRAD | LIT 225kV N0 1 GANGES - VIRADEL | GANGES | GANGE | VIRADEL | VIRAD | 225 | 302 | 424 | 424 | 531 |  |  | 6.56 | 23.93 | 505.82 | 79.454 | 58068
GARCHL61SSELO | LIT 225kV N0 1 GARCHIZY-ST-ELOI | GARCHIZY | GARCH | ST-ELOI | SSELO | 225 | 814 | 930 | 983 | 1099 |  |  | 0.689 | 4.611 | 189.365 | 29.745 | 12095
GAVREL61ZTRAN | LIT 225kV N0 1 GAVRELLE - TRAN5 / GAVRE PERTA 1 | GAVRELLE | GAVRE |  | ZTRAN | 225 | 956 | 1110 | 1110 | 1088 |  |  | 3.154 | 14.315 | 307.156 | 48.248 | 34720
GEN.PL61IZERN | LIT 225kV N0 1 GENISSIAT-POSTE-IZERNORE | GENISSIAT-POSTE | GEN.P | IZERNORE | IZERN | 225 | 862 | 928 | 928 | 987 |  |  | 1.928 | 9.402 | 347.817 | 54.635 | 27258
GEN.PL61SERRI | LIT 225kV N0 1 GENISSIAT-POSTE-SERRIERES | GENISSIAT-POSTE | GEN.P | SERRIERES | SERRI | 225 | 477 | 566 | 566 | 642 |  |  | 1.98 | 8.5 | 178.726 | 28 | 20269
GEN.PL61VOUGL | LIT 225kV N0 1 GENISSIAT-POSTE-VOUGLANS | GENISSIAT-POSTE | GEN.P | VOUGLANS | VOUGL | 225 | 853 | 991 | 991 | 1118 |  |  | 2.558 | 15.756 | 370.14 | 58.141 | 40005
GINESL61LESQU | LIT 225kV N0 1 GINESTOUS-LESQUIVE | GINESTOUS | GINES | LESQUIVE | LESQU | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 1.645 | 10.967 | 252.095 | 39.599 | 27394
GIVORL61MIONS | LIT 225kV N0 1 GIVORS - MIONS | GIVORS | GIVOR | MIONS | MIONS | 225 | 695 | 782 | 782 | 940 |  |  | 1.62 | 8.05 | 226.553 | 35 | 19391
G.BANL61GIVOR | LIT 225kV N0 1 GIVORS-BANS-GIVORS | GIVORS-BANS | G.BAN | GIVORS | GIVOR | 225 | 900 | 1015 | 1015 | 1112 |  |  | 0.02 | 0.19 | 5.606 | 0 | 558
GODINL61RUEYR | LIT 225kV N0 1 GODIN-RUEYRES | GODIN | GODIN | RUEYRES | RUEYR | 225 | 637 | 706 | 706 | 793 |  |  | 4.693 | 19.594 | 400.112 | 62.849 | 46373
GODINL61SSVIC | LIT 225kV N0 1 GODIN-ST-VICTOR | GODIN | GODIN | ST-VICTOR | SSVIC | 225 | 442 | 511 | 511 | 577 |  |  | 11.175 | 31.341 | 635.67 | 99.851 | 74374
GODINL61VERLH | LIT 225kV N0 1 GODIN-VERLHAGUET | GODIN | GODIN | VERLHAGUET | VERLH | 225 | 819 | 897 | 897 | 974 |  |  | 8.815 | 41.177 | 832.318 | 130.74 | 96865
GOURJL61VERFE | LIT 225kV N0 1 GOURJADE - VERFEIL | GOURJADE | GOURJ | VERFEIL | VERFE | 225 | 828 | 908 | 908 | 986 |  |  | 5.828 | 28.348 | 631.062 | 99.127 | 69653
GRAFFL61MARL6 | LIT 225kV N0 1 GRAFFENSTADEN-MARLENHEIM | GRAFFENSTADEN | GRAFF | MARLENHEIM | MARL6 | 225 | 843 | 909 | 909 | 996 |  |  | 1.507 | 7.466 | 165.192 | 25.948 | 18385
GRAFFL61SCHEE | LIT 225kV N0 1 GRAFFENSTADEN-SCHEER | GRAFFENSTADEN | GRAFF | SCHEER | SCHEE | 225 | 654 | 758 | 758 | 857 |  |  | 2.123 | 9.657 | 210.668 | 33.092 | 23641
G.COUL61ROUGE | LIT 225kV N0 1 GRAND-COURONNE-ROUGEMONTIER | GRAND-COURONNE | G.COU | ROUGEMONTIER | ROUGE | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.423 | 9.529 | 217.498 | 34.165 | 23798
G.COUL61SSROU | LIT 225kV N0 1 GRAND-COURONNE-ST ETIENNE DU ROUVRAY | GRAND-COURONNE | G.COU | ST ETIENNE DU ROUVRAY | SSROU | 225 | 1300 | 1350 | 1350 | 1400 |  |  | 0.544 | 3.646 | 83.153 | 13.062 | 9071
G.COUL61VAUPA | LIT 225kV N0 1 GRAND-COURONNE-VAUPALIERE (LA) | GRAND-COURONNE | G.COU | VAUPALIERE (LA) | VAUPA | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.559 | 10.443 | 236.753 | 37.189 | 25989
G.SYNL61HOLQU | LIT 225kV N0 1 GRANDE-SYNTHE-HOLQUE | GRANDE-SYNTHE | G.SYN | HOLQUE | HOLQU | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.146 | 7.622 | 175.943 | 27.637 | 19435
G.SYNL61WARAN | LIT 225kV N0 1 GRANDE-SYNTHE-WARANDE | GRANDE-SYNTHE | G.SYN | WARANDE | WARAN | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.884 | 5.897 | 135.526 | 21.288 | 14722
G.QUEL61VAUPA | LIT 225kV N0 1 GRAND-QUEVILLY-VAUPALIERE (LA) | GRAND-QUEVILLY | G.QUE | VAUPALIERE (LA) | VAUPA | 225 | 820 | 820 | 1040 | 1040 |  |  | 0.56 | 3.82 | 234.734 | 35 | 9478
GRANDL61PRATC | LIT 225kV N0 1 GRANDVAL-PRATCLAUX | GRANDVAL | GRAND | PRATCLAUX | PRATC | 225 | 790 | 790 | 862 | 926 |  |  | 4.456 | 19.925 | 430.568 | 67.633 | 49036
GRANZL61NIORT | LIT 225kV N0 1 GRANZAY-NIORT | GRANZAY | GRANZ | NIORT | NIORT | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 1.599 | 10.685 | 243.614 | 38.267 | 26683
GRANZL61SSFLO | LIT 225kV N0 1 GRANZAY-ST-FLORENT | GRANZAY | GRANZ | ST-FLORENT | SSFLO | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 0.644 | 4.29 | 98.733 | 15.509 | 10767
GREZIL61ZFONC | LIT 225kV N0 1 GREZILLAC - PIQUAGE A FONCROSE | GREZILLAC | GREZI |  | ZFONC | 225 | 932 | 1049 | 1049 | 1126 |  |  | 0.955 | 6.332 | 146.681 | 23.041 | 16000
GRIM5L61TRANS | LIT 225KV N0 1 GRIMAUD - TRANS | GRIMAUD | GRIM5 | TRANS | TRANS | 225 | [6 empty] | 1.682 | 11.13 | 986.374 | 154.939 | 29772
GRISOL61S.PON | LIT 225kV N0 1 GRISOLLES-SERRE-PONCON | GRISOLLES | GRISO | SERRE-PONCON | S.PON | 225 | 1059 | 1141 | 1141 | 1215 |  |  | 1.064 | 6.729 | 155.739 | 24.463 | 17195
G.CAIL61MASTA | LIT 225kV N0 1 GROS-CAILLOU-MASTAING | GROS-CAILLOU | G.CAI | MASTAING | MASTA | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.253 | 1.676 | 38.835 | 6.1 | 4208
GROSNL61GUEUG | LIT 225kV N0 1 GROSNE-GUEUGNON | GROSNE | GROSN | GUEUGNON | GUEUG | 225 | 814 | 983 | 983 | 1099 |  |  | 3.29 | 21.899 | 504.909 | 79.311 | 54965
GROSNL61MACON | LIT 225kV N0 1 GROSNE-MACON | GROSNE | GROSN | MACON | MACON | 225 | 618 | 718 | 718 | 807 |  |  | 1.892 | 19.148 | 684.552 | 107.529 | 59040
GUEBWL61LOGEL | LIT 225kV N0 1 GUEBWILLER - LOGELBACH | GUEBWILLER | GUEBW | LOGELBACH | LOGEL | 225 | 1070 | 1155 | 1155 | 1265 |  |  | 1.722 | 11.524 | 259.905 | 40.826 | 28559
GUEBWL61VOGEL | LIT 225kV N0 1 GUEBWILLER - VOGELGRUN | GUEBWILLER | GUEBW | VOGELGRUN | VOGEL | 225 | 1070 | 1155 | 1155 | 1265 |  |  | 2.087 | 13.943 | 313.035 | 49.171 | 34526
GUEUGL61H.PAU | LIT 225kV N0 1 GUEUGNON - HENRI-PAUL | GUEUGNON | GUEUG | HENRI-PAUL | H.PAU | 225 | 715 | 897 | 897 | 1032 |  |  | 2.391 | 15.925 | 541.805 | 85.107 | 40553
GUPIEL61ZFONC | LIT 225kV N0 1 GUPIE - PIQUAGE A FONCROSE | GUPIE | GUPIE |  | ZFONC | 225 | 831 | 984 | 984 | 1099 |  |  | 1.68 | 11.144 | 258.16 | 40.552 | 28000
HAVR5L61P.SEP | LIT 225kV N0 1 HAVRE (LE) (POSTE) - PONT-SEPT | HAVRE (LE) (POSTE) | HAVR5 | PONT-SEPT | P.SEP | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 0.119 | 1.154 | 49.639 | 7.797 | 3952
HOLQUL61LONG9 | LIT 225kV N0 1 HOLQUE-LONGUENESSE | HOLQUE | HOLQU | LONGUENESSE | LONG9 | 225 | 969 | 969 | 1061 | 1061 |  |  | 0.782 | 5.214 | 149.229 | 23.441 | 12938
HOLQUL61WARAN | LIT 225kV N0 1 HOLQUE-WARANDE | HOLQUE | HOLQU | WARANDE | WARAN | 225 | 1300 | 1350 | 1350 | 1400 |  |  | 1.263 | 8.407 | 193.563 | 30.405 | 21021
HOURAL61MARSI | LIT 225kV N0 1 HOURAT (LE)-MARSILLON | HOURAT (LE) | HOURA | MARSILLON | MARSI | 225 | 419 | 580 | 580 | 720 |  |  | 4.321 | 19.708 | 426.327 | 66.967 | 48124
HOURAL61MIEGE | LIT 225kV N0 1 HOURAT (LE)-MIEGEBAT | HOURAT (LE) | HOURA | MIEGEBAT | MIEGE | 225 | 392 | 542 | 542 | 673 |  |  | 0.556 | 2.595 | 53.971 | 8.478 | 6195
I.NAPL61OTTMA | LIT 225kV N0 1 ILE-NAPOLEON - OTTMARSHEIM | ILE-NAPOLEON | I.NAP | OTTMARSHEIM | OTTMA | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 0.673 | 4.467 | 103.485 | 16.255 | 11225
I.NAPL61LUTTE | LIT 225kV N0 1 ILE-NAPOLEON-LUTTERBACH | ILE-NAPOLEON | I.NAP | LUTTERBACH | LUTTE | 225 | 847 | 985 | 985 | 1116 |  |  | 1.107 | 7.448 | 167.426 | 26.299 | 18460
ISSOIL61LIGNA | LIT 225kV N0 1 ISSOIRE-LIGNAT | ISSOIRE | ISSOI | LIGNAT | LIGNA | 225 | 1002 | 1113 | 1113 | 1205 |  |  | 1.28 | 8.47 | 186.049 | 30 | 20903
ISSOIL61PRATC | LIT 225kV N0 1 ISSOIRE-PRATCLAUX | ISSOIRE | ISSOI | PRATCLAUX | PRATC | 225 | 770 | 928 | 928 | 1037 |  |  | 4.546 | 30.66 | 657.513 | 103.282 | 74277
JACQUL61SOLEI | LIT 225kV N0 1 JACQUARD-SOLEIL (LE) | JACQUARD | JACQU | SOLEIL (LE) | SOLEI | 225 | 1123 | 1211 | 1211 | 1290 |  |  | 1.008 | 6.752 | 154.06 | 24.2 | 16737
JALISL61LESQU | LIT 225kV N0 1 JALIS-LESQUIVE | JALIS | JALIS | LESQUIVE | LESQU | 225 | 828 | 908 | 908 | 986 |  |  | 5.569 | 28.651 | 645.487 | 101.393 | 71153
JONQUL61SSCES | LIT 225kV N0 1 JONQUIERES-ST-CESAIRE | JONQUIERES | JONQU | ST-CESAIRE | SSCES | 225 | 1055 | 1055 | 1230 | 1230 |  |  | 1.244 | 8.273 | 223.516 | 35.11 | 21709
KEMBSL61OTTMA | LIT 225kV N0 1 KEMBS-OTTMARSHEIM | KEMBS | KEMBS | OTTMARSHEIM | OTTMA | 225 | 539 | 661 | 661 | 754 |  |  | 1.24 | 5.637 | 125.847 | 19.768 | 13944
KEMBSL61SIERE | LIT 225kV N0 1 KEMBS-SIERENTZ | KEMBS | KEMBS | SIERENTZ | SIERE | 225 | 827 | 891 | 891 | 976 |  |  | 0.335 | 1.586 | 33.406 | 5.247 | 3807
GAUDIL61LIVIE | LIT 225kV N0 1 LA GAUDIERE - LIVIERE | GAUDIERE (LA) | GAUDI | LIVIERE | LIVIE | 225 | 1090 | 1090 | 1260 | 1260 |  |  | 0.821 | 5.543 | 512.758 | 80.544 | 26831
GAUDIL61MOREA | LIT 225kV N0 1 LA GAUDIERE - MOREAU | GAUDIERE (LA) | GAUDI | MOREAU | MOREA | 225 | 946 | 1010 | 1010 | 1063 |  |  | 2.208 | 9.825 | 217.855 | 34.221 | 24262
GAUDIL61SSVIN | LIT 225kV N0 1 LA GAUDIERE - ST VINCENT | GAUDIERE (LA) | GAUDI | ST-VINCENT | SSVIN | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 3.26 | 22.082 | 507.881 | 79.778 | 55078
LANDEL61LOSCO | LIT 225kV N0 1 LANDERNEAU-LOSCOAT | LANDERNEAU | LANDE | LOSCOAT | LOSCO | 225 | 1212 | 1262 | 1262 | 1318 |  |  | 1.551 | 10.314 | 237.566 | 37.317 | 25862
LANDEL61MARTY | LIT 225kV N0 1 LANDERNEAU-MARTYRE (LA) | LANDERNEAU | LANDE | MARTYRE (LA) | MARTY | 225 | 1217 | 1266 | 1266 | 1322 |  |  | 0.222 | 1.324 | 31.132 | 4.89 | 3870
LANDRL61MTOIS | LIT 225kV N0 1 LANDRES-MONTOIS | LANDRES | LANDR | MONTOIS | MTOIS | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 1.396 | 9.385 | 215.504 | 33.851 | 23325
LANDRL61MOULA | LIT 225kV N0 1 LANDRES-MOULAINE | LANDRES | LANDR | MOULAINE | MOULA | 225 | 1070 | 1155 | 1155 | 1265 |  |  | 1.207 | 8.015 | 176.797 | 27.771 | 19700
LANDRL61STENA | LIT 225kV N0 1 LANDRES-STENAY | LANDRES | LANDR | STENAY | STENA | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 2.804 | 19.287 | 453.32 | 71.207 | 49025
LANDRL61VIGY | LIT 225kV N0 1 LANDRES-VIGY | LANDRES | LANDR |  | 1VIGY | 225 | 1070 | 1155 | 1155 | 1265 |  |  | 2.59 | 17.345 | 395.623 | 62.144 | 43185
LANNEL61PRAGN | LIT 225kV N0 1 LANNEMEZAN-PRAGNERES | LANNEMEZAN | LANNE | PRAGNERES | PRAGN | 225 | 737 | 820 | 820 | 889 |  |  | 5.673 | 25.457 | 565.026 | 88.754 | 62874
LATENL61PERTA | LIT 225kV N0 1 LATENA-PERTAIN | LATENA | LATEN | PERTAIN | PERTA | 225 | 1172 | 1235 | 1285 | 1388 |  |  | 1.003 | 6.694 | 196.022 | 30.791 | 16987
LATENL61ROYE | LIT 225kV N0 1 LATENA-ROYE | LATENA | LATEN |  | 1ROYE | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.65 | 4.449 | 103.976 | 16.333 | 11268
LAUNAL61RAN.P | LIT 225kV N0 1 LAUNAY-RANCE-POSTE | LAUNAY | LAUNA | RANCE-POSTE | RAN.P | 225 | 901 | 988 | 988 | 1050 |  |  | 5.956 | 27.074 | 597.91 | 93.919 | 66725
LAVERL61PONTE | LIT 225kV N0 1 LAVERA - PONTEAU | LAVERA | LAVER | PONTEAU | PONTE | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 0.063 | 0.696 | 33.918 | 5.328 | 2540
LAVERL61SEPTE | LIT 225kV N0 1 LAVERA - SEPTEMES | LAVERA | LAVER | SEPTEMES | SEPTE | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.732 | 11.488 | 266.09 | 41.797 | 28904
LAVERL61P.BOU | LIT 225kV N0 1 LAVERA-PORT-DE-BOUC (CLIENT) | LAVERA | LAVER | PORT-DE-BOUC (CLIENT) | P.BOU | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.526 | 3.524 | 80.894 | 12.707 | 8816
LAVEYL61PRATC | LIT 225kV N0 1 LAVEYRUNE - PRATCLAUX | LAVEYRUNE | LAVEY | PRATCLAUX | PRATC | 225 | 315 | 443 | 443 | 546 |  |  | 6.679 | 19.423 | 385.704 | 60.586 | 45190
LEGUEL61P.SIM | LIT 225kV N0 1 LEGUEVIN - PORTET-ST-SIMON | LEGUEVIN | LEGUE | PORTET-ST-SIMON | P.SIM | 225 | 813 | 890 | 890 | 966 |  |  | 1.616 | 7.481 | 157.241 | 24.699 | 17986
LEGUEL61LESQU | LIT 225kV N0 1 LEGUEVIN-LESQUIVE | LEGUEVIN | LEGUE | LESQUIVE | LESQU | 225 | 813 | 890 | 890 | 966 |  |  | 2.266 | 10.729 | 226.621 | 35.598 | 24939
LESCAL61MARSI | LIT 225KV N0 1 LESCAR - MARSILLON | LESCAR | LESCA | MARSILLON | MARSI | 225 | 1172 | 1248 | 1248 | 1310 |  |  | 1.083 | 7.281 | 247.831 | 38.929 | 18300
LESQUL61VERLH | LIT 225kV N0 1 LESQUIVE-VERLHAGUET | LESQUIVE | LESQU | VERLHAGUET | VERLH | 225 | 828 | 908 | 908 | 986 |  |  | 2.045 | 9.143 | 217.741 | 34.203 | 24271
LIGNAL61RULHA | LIT 225kV N0 1 LIGNAT-RULHAT | LIGNAT | LIGNA | RULHAT | RULHA | 225 | 1032 | 1146 | 1146 | 1241 |  |  | 0.633 | 4.196 | 91.369 | 14.352 | 10255
LINGOL61T.VIC | LIT 225kV N0 1 LINGOSTIERE-TRINITE-VICTOR | LINGOSTIERE | LINGO | TRINITE-VICTOR | T.VIC | 225 | 816 | 889 | 889 | 947 |  |  | 1.092 | 4.937 | 109.7 | 17.279 | 12188
LIVIEL61SSVIN | LIT 225kV N0 1 LIVIERE - ST VINCENT | LIVIERE | LIVIE | ST-VINCENT | SSVIN | 225 | 1234 | 1320 | 1320 | 1389 |  |  | 1.661 | 11.463 | 263.185 | 41.341 | 28524
L.CHAL61S.DAM | LIT 225kV N0 1 LONG-CHAMP (LE) - SOISSONS-NOTRE-DAME | LONG-CHAMP (LE) | L.CHA | SOISSONS-NOTRE-DAME | S.DAM | 225 | 731 | 835 | 835 | 925 |  |  | 1.112 | 5.351 | 117.783 | 18.501 | 13165
LOSCOL61MARTY | LIT 225kV N0 1 LOSCOAT-MARTYRE (LA) | LOSCOAT | LOSCO | MARTYRE (LA) | MARTY | 225 | 1280 | 1332 | 1332 | 1382 |  |  | 1.705 | 11.348 | 261.392 | 41.059 | 29488
LUMESL61MAZUR | LIT 225kV N0 1 LUMES-MAZURES | LUMES | LUMES | MAZURES | MAZUR | 225 | 843 | 909 | 909 | 996 |  |  | 1.937 | 9.449 | 211.15 | 33.167 | 23715
LUMESL61MOHON | LIT 225kV N0 1 LUMES-MOHON | LUMES | LUMES | MOHON | MOHON | 225 | 647 | 749 | 749 | 847 |  |  | 0.395 | 1.79 | 38.503 | 6.048 | 4700
LUMESL61STENA | LIT 225kV N0 1 LUMES-STENAY | LUMES | LUMES | STENAY | STENA | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 2.551 | 17.609 | 407.938 | 64.079 | 44900
LUTTEL61SIERE | LIT 225kV N0 1 LUTTERBACH-SIERENTZ | LUTTERBACH | LUTTE | SIERENTZ | SIERE | 225 | 847 | 985 | 985 | 1116 |  |  | 1.375 | 9.214 | 210.165 | 33.013 | 22900
MALGOL61PASSY | LIT 225kV N0 1 MALGOVERT-PASSY | MALGOVERT | MALGO | PASSY | PASSY | 225 | 533 | 622 | 622 | 673 |  |  | 4.59 | 14.74 | 305.729 | 48 | 35004
MALINL61SARR5 | LIT 225KV N0 1 MALINTRAT - SARRE | MALINTRAT | MALIN | SARRE | SARR5 | 225 | [6 empty] | 0.204 | 1.618 | 2561.363 | 402.338 | 10717
MALINL61RULHA | LIT 225kV N0 1 MALINTRAT-RULHAT | MALINTRAT | MALIN | RULHAT | RULHA | 225 | 1034 | 1149 | 1149 | 1244 |  |  | 0.355 | 2.328 | 51.856 | 8.146 | 5747
MAMBEL61SAONE | LIT 225kV N0 1 MAMBELIN - SAONE | MAMBELIN | MAMBE | SAONE | SAONE | 225 | 801 | 930 | 930 | 1053 |  |  | 2.786 | 17.707 | 412.179 | 64.745 | 44648
MAMBEL61PALEN | LIT 225kV N0 1 MAMBELIN-PALENTE | MAMBELIN | MAMBE | PALENTE | PALEN | 225 | 577 | 706 | 706 | 782 |  |  | 6.326 | 22.083 | 462.694 | 72.68 | 52934
MAMBEL61PTARL | LIT 225kV N0 1 MAMBELIN-PONTARLIER | MAMBELIN | MAMBE | PONTARLIER | PTARL | 225 | 412 | 449 | 449 | 449 |  |  | 9.519 | 35.036 | 774.911 | 121.723 | 86680
MAMBEL61PUSY | LIT 225kV N0 1 MAMBELIN-PUSY | MAMBELIN | MAMBE |  | 1PUSY | 225 | 525 | 730 | 730 | 835 |  |  | 6.231 | 31.693 | 697.642 | 109.585 | 77914
MANOIL61SSBAI | LIT 225kV N0 1 MANOIR (LE)-ST-PIERRE-DE-BAILLEUL | MANOIR (LE) | MANOI | ST-PIERRE-DE-BAILLEUL | SSBAI | 225 | 757 | 946 | 946 | 1075 |  |  | 2.544 | 16.971 | 379.507 | 59.613 | 41848
MARGEL61PRATC | LIT 225kV N0 1 MARGERIDE-PRATCLAUX | MARGERIDE | MARGE | PRATCLAUX | PRATC | 225 | 792 | 844 | 844 | 905 |  |  | 3.738 | 15.121 | 356.139 | 55.942 | 38458
MARGEL61RUEYR | LIT 225kV N0 1 MARGERIDE-RUEYRES | MARGERIDE | MARGE | RUEYRES | RUEYR | 225 | 802 | 844 | 844 | 919 |  |  | 4.645 | 19.038 | 432.705 | 67.969 | 47388
MARMAL61VARE5 | LIT 225kV N0 1 MARMAGNE-VARENNES (-SUR-FOUZON) | MARMAGNE | MARMA | VARENNES (-SUR-FOUZON) | VARE5 | 225 | 409 | 644 | 644 | 761 |  |  | 4.746 | 21.572 | 476.126 | 74.79 | 53196
MARSIL61PRAGN | LIT 225kV N0 1 MARSILLON-PRAGNERES | MARSILLON | MARSI | PRAGNERES | PRAGN | 225 | 565 | 673 | 673 | 765 |  |  | 7.841 | 34.13 | 756.39 | 118.814 | 84292
MARTYL61SQUIV | LIT 225kV N0 1 MARTYRE (LA)-SQUIVIDAN | MARTYRE (LA) | MARTY | SQUIVIDAN | SQUIV | 225 | 1056 | 1123 | 1123 | 1189 |  |  | 3.038 | 20.399 | 472.264 | 74.183 | 51302
MASTAL61PERIZ | LIT 225kV N0 1 MASTAING-PERIZET (LE) | MASTAING | MASTA | PERIZET (LE) | PERIZ | 225 | 975 | 1030 | 1030 | 1110 |  |  | 2.219 | 10.244 | 226.917 | 35.644 | 24738
MASTAL61P.SAM | LIT 225kV N0 1 MASTAING-PONT-SUR-SAMBRE | MASTAING | MASTA | PONT-SUR-SAMBRE | P.SAM | 225 | 975 | 976 | 1030 | 1104 |  |  | 3.865 | 17.913 | 421.04 | 66.137 | 44098
MAUBEL61P.SAM | LIT 225kV N0 1 MAUBEUGE-PONT-SUR-SAMBRE | MAUBEUGE | MAUBE | PONT-SUR-SAMBRE | P.SAM | 225 | 956 | 1010 | 1010 | 1088 |  |  | 0.588 | 2.808 | 62.855 | 9.873 | 6968
MAUGEL61VERTO | LIT 225kV N0 1 MAUGES (LES)-VERTOU | MAUGES (LES) | MAUGE | VERTOU | VERTO | 225 | 488 | 682 | 682 | 795 |  |  | 4.191 | 19.19 | 418.254 | 65.699 | 47048
MAUREL61P.CHA | LIT 225kV N0 1 MAUREIX (LE)-PEYRAT-LE-CHATEAU | MAUREIX (LE) | MAURE | PEYRAT-LE-CHATEAU | P.CHA | 225 | 725 | 800 | 800 | 865 |  |  | 2.673 | 14.733 | 311.556 | 48.939 | 35567
MERLAL61RECOU | LIT 225kV N0 1 MERLATIERE - RECOUVRANCE | MERLATIERE | MERLA | RECOUVRANCE | RECOU | 225 | 870 | 870 | 1180 | 1180 |  |  | 0.743 | 5.816 | 10449.986 | 1641.48 | 35439
MERLAL61SOULL | LIT 225kV N0 1 MERLATIERE - SOULLANS | MERLATIERE | MERLA | SOULLANS | SOULL | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 2.603 | 17.492 | 395.897 | 62.187 | 43410
MEZE5L61PORCH | LIT 225kV N0 1 MEZEROLLES - PORCHEVILLE | MEZEROLLES | MEZE5 | PORCHEVILLE | PORCH | 225 | 520 | 782 | 782 | 998 |  |  | 0.371 | 2.449 | 56.301 | 8.844 | 6148
MIONSL61MOIRA | LIT 225kV N0 1 MIONS-MOIRANS | MIONS | MIONS | MOIRANS | MOIRA | 225 | 579 | 672 | 672 | 755 |  |  | 5.95 | 27.53 | 606.966 | 92 | 67808
MIONSL61MOUCH | LIT 225kV N0 1 MIONS-MOUCHE (LA) | MIONS | MIONS | MOUCHE (LA) | MOUCH | 225 | 1800 | 2030 | 2030 | 2224 |  |  | 0.42 | 4.24 | 179.376 | 26 | 13700
MIONSL61P.EVE | LIT 225kV N0 1 MIONS-PONT-EVEQUE | MIONS | MIONS | PONT-EVEQUE | P.EVE | 225 | 880 | 992 | 992 | 1086 |  |  | 1.22 | 8.32 | 172.457 | 27 | 18949
MIONSL61SSV.E | LIT 225kV N0 1 MIONS-ST-VULBAS-EST | MIONS | MIONS | ST-VULBAS-EST | SSV.E | 225 | 297 | 442 | 442 | 545 |  |  | 3.84 | 14.24 | 291.403 | 45 | 33600
MIONSL61VENIS | LIT 225kV N0 1 MIONS-VENISSIEUX | MIONS | MIONS | VENISSIEUX | VENIS | 225 | 900 | 1015 | 1015 | 1112 |  |  | 0.33 | 3.01 | 159.383 | 17 | 9344
M.MORL61SAUS5 | LIT 225kV N0 1 MITRY-MORY (E.D.F.)-SAUSSET | MITRY-MORY (E.D.F.) | M.MOR | SAUSSET | SAUS5 | 225 | 731 | 835 | 835 | 930 |  |  | 0.397 | 1.989 | 44.663 | 7.016 | 4933
M.MORL61VLEVA | LIT 225kV N0 1 MITRY-MORY (E.D.F.)-VILLEVAUDE | MITRY-MORY (E.D.F.) | M.MOR | VILLEVAUDE | VLEVA | 225 | 899 | 984 | 984 | 1061 |  |  | 0.727 | 3.391 | 75.548 | 11.867 | 8375
MOIMOL61P.GAS | LIT 225kV N0 1 MOIMONT - PLESSIS-GASSOT | MOIMONT | MOIMO | PLESSIS-GASSOT | P.GAS | 225 | 716 | 817 | 817 | 910 |  |  | 0.867 | 4.462 | 128.145 | 20.129 | 10848
MOLE L61RUEYR | LIT 225kV N0 1 MOLE (LA)-RUEYRES | MOLE (LA) | MOLE | RUEYRES | RUEYR | 225 | 622 | 748 | 748 | 834 |  |  | 7.221 | 34.122 | 706.313 | 110.947 | 81267
MOLE L61SSFEY | LIT 225kV N0 1 MOLE (LA)-STE-FEYRE | MOLE (LA) | MOLE | STE-FEYRE | SSFEY | 225 | 578 | 694 | 694 | 774 |  |  | 8.123 | 41.941 | 980.672 | 154.044 | 105922
MTCROL61VENDI | LIT 225kV N0 1 MONTCROISETTE-VENDIN | MONTCROISETTE | MTCRO | VENDIN | VENDI | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.293 | 1.942 | 44.991 | 7.067 | 4880
MTGROL61MTPEZ | LIT 225KV N0 1 MONTGROS - MONTPEZAT | MONTGROS | MTGRO | MONTPEZAT | MTPEZ | 225 | 370 | 559 | 559 | 695 |  |  | 4.023 | 18.8 | 691.465 | 108.615 | 45680
MTGROL61PRATC | LIT 225KV N0 1 MONTGROS - PRATCLAUX | MONTGROS | MTGRO | PRATCLAUX | PRATC | 225 | 346 | 524 | 524 | 649 |  |  | 1.973 | 9.26 | 524.356 | 82.366 | 22994
MTLUCL61MTVIC | LIT 225kV N0 1 MONTLUCON-MONTVICQ | MONTLUCON | MTLUC | MONTVICQ | MTVIC | 225 | 555 | 692 | 692 | 790 |  |  | 1.752 | 7.035 | 154.337 | 24.243 | 17280
MTOISL61SSHUB | LIT 225kV N0 1 MONTOIS-SAINT HUBERT | MONTOIS | MTOIS | SAINT HUBERT | SSHUB | 225 | 456 | 556 | 556 | 634 |  |  | 1.92 | 6.187 | 125.097 | 19.65 | 14580
MTPELL61TAMAR | LIT 225kV N0 1 MONTPELLIER - TAMAREAU | MONTPELLIER | MTPEL | TAMAREAU | TAMAR | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.217 | 8.128 | 186.513 | 29.297 | 20339
MTPEZL61PRATC | LIT 225kV N0 1 MONTPEZAT-PRATCLAUX | MONTPEZAT | MTPEZ | PRATCLAUX | PRATC | 225 | 346 | 524 | 524 | 649 |  |  | 5.976 | 26.796 | 592.563 | 93.08 | 66141
MORBRL61V.GEO | LIT 225kV N0 1 MORBRAS-VILLENEUVE-ST-GEORGES | MORBRAS | MORBR | VILLENEUVE-ST-GEORGES | V.GEO | 225 | 886 | 886 | 984 | 1061 |  |  | 1.37 | 6.904 | 476.325 | 74.821 | 18381
MOUGIL61P.GR5 | LIT 225kV N0 1 MOUGINS-PLAN-DE-GRASSE | MOUGINS | MOUGI | PLAN-DE-GRASSE | P.GR5 | 225 | 1000 | 1000 | 1160 | 1185 |  |  | 0.584 | 4.203 | 414.298 | 65.078 | 12987
MOUL8L61VLEJU | LIT 225kV N0 1 MOULINEAUX - VILLEJUST | MOULINEAUX | MOUL8 | VILLEJUST | VLEJU | 225 | 750 | 750 | 1030 | 1030 |  |  | 0.581 | 5.531 | 1074.57 | 168.793 | 21407
MUREAL61NOURO | LIT 225kV N0 1 MUREAUX (LES) - NOUROTTES | MUREAUX (LES) | MUREA | NOUROTTES | NOURO | 225 | 1172 | 1172 | 1285 | 1388 |  |  | 0.687 | 4.587 | 140.823 | 22.12 | 11647
NEMOUL61VLEMA | LIT 225kV N0 1 NEMOURS-VILLEMANDEUR | NEMOURS | NEMOU | VILLEMANDEUR | VLEMA | 225 | 520 | 782 | 782 | 998 |  |  | 1.682 | 11.498 | 260.862 | 40.976 | 28561
NEOULL61VINS | LIT 225kV N0 1 NEOULES-VINS | NEOULES | NEOUL |  | 1VINS | 225 | 1057 | 1057 | 1160 | 1224 |  |  | 1.669 | 11.088 | 292.225 | 45.903 | 27764
NIORTL61V.SEV | LIT 225kV N0 1 NIORT - VAL-DE-SEVRE | NIORT | NIORT | VAL-DE-SEVRE | V.SEV | 225 | 803 | 858 | 858 | 918 |  |  | 6.196 | 22.472 | 466.824 | 73.329 | 52463
NOGENL61ORMES | LIT 225kV N0 1 NOGENTEL-ORMES | NOGENTEL | NOGEN | ORMES | ORMES | 225 | 1172 | 1285 | 1285 | 1375 |  |  | 3.502 | 23.311 | 538.177 | 84.537 | 57945
O.CHAL61RUEYR | LIT 225kV N0 1 ONET-LE-CHATEAU-RUEYRES | ONET-LE-CHATEAU | O.CHA | RUEYRES | RUEYR | 225 | 902 | 1004 | 1004 | 1131 |  |  | 2.935 | 20.096 | 455.028 | 71.476 | 49985
MONDIL61ORANG | LIT 225kV N0 1 ORANGERIE (L) - MONDION | MONDION | MONDI | ORANGERIE (L) | ORANG | 225 | 957 | 1023 | 1023 | 1096 |  |  | 1.277 | 5.906 | 131.562 | 20.666 | 14139
PALENL61SAONE | LIT 225kV N0 1 PALENTE -SAONE | PALENTE | PALEN | SAONE | SAONE | 225 | 928 | 1001 | 1001 | 1096 |  |  | 0.565 | 3.201 | 72.671 | 11.415 | 7958
PALUNL61SSTUL | LIT 225kV N0 1 PALUN (LA) - SAINTE-TULLE 1 | PALUN (LA) | PALUN | STE-TULLE | SSTUL | 225 | 816 | 889 | 889 | 947 |  |  | 3.511 | 18.486 | 415.598 | 65.282 | 45834
PALUNL61SEPTE | LIT 225kV N0 1 PALUN (LA)-SEPTEMES | PALUN (LA) | PALUN | SEPTEMES | SEPTE | 225 | 1375 | 1437 | 1437 | 1500 |  |  | 0.524 | 6.439 | 153.451 | 24.104 | 16137
PASSYL61PRESS | LIT 225kV N0 1 PASSY-PRESSY | PASSY | PASSY | PRESSY | PRESS | 225 | 619 | 687 | 687 | 744 |  |  | 2.315 | 10.285 | 254.3 | 39.945 | 26303
PATISL61REMIS | LIT 225kV N0 1 PATIS - REMISE | PATIS | PATIS | REMISE | REMIS | 225 | 1035 | 1035 | 1235 | 1235 |  |  | 1.164 | 7.763 | 304.123 | 47.771 | 19879
PATISL61TERRI | LIT 225kV N0 1 PATIS-TERRIER | PATIS | PATIS | TERRIER | TERRI | 225 | 910 | 910 | 1105 | 1105 |  |  | 1.426 | 9.744 | 300.57 | 47.213 | 25455
PELISL61SSVIC | LIT 225kV N0 1 PELISSIER-ST-VICTOR | PELISSIER | PELIS | ST-VICTOR | SSVIC | 225 | 1018 | 1117 | 1117 | 1213 |  |  | 3.91 | 22.5 | 518.7 | 81 | 55118
PERIZL61SETIE | LIT 225kV N0 1 PERIZET (LE)-SETIER | PERIZET (LE) | PERIZ | SETIER | SETIE | 225 | 579 | 709 | 709 | 822 |  |  | 2.404 | 11.2 | 237.925 | 37.373 | 27058
PERTAL61ROYE | LIT 225kV N0 1 PERTAIN-ROYE | PERTAIN | PERTA |  | 1ROYE | 225 | 566 | 692 | 692 | 802 |  |  | 1.083 | 4.936 | 160.31 | 25.181 | 12168
PESSAL61SAUCA | LIT 225kV N0 1 PESSAC-SAUCATS | PESSAC | PESSA | SAUCATS | SAUCA | 225 | 938 | 980 | 1055 | 1132 |  |  | 1.234 | 8.332 | 197.276 | 30.988 | 21293
P.ROSL61SARR6 | LIT 225kV N0 1 PETITE-ROSSELLE-SARREGUEMINES | PETITE-ROSSELLE | P.ROS | SARREGUEMINES | SARR6 | 225 | 843 | 909 | 909 | 996 |  |  | 1.985 | 10.313 | 232.259 | 36.483 | 24575
P.ROSL61SSAVO | LIT 225kV N0 1 PETITE-ROSSELLE-ST-AVOLD | PETITE-ROSSELLE | P.ROS | ST-AVOLD | SSAVO | 225 | 715 | 715 | 840 | 840 |  |  | 1.424 | 6.322 | 200.082 | 31.429 | 15830
P.BORL61PRATC | LIT 225kV N0 1 PIED-DE-BORNE - PRATCLAUX | PIED-DE-BORNE | P.BOR | PRATCLAUX | PRATC | 225 | 315 | 400 | 400 | 493 |  |  | 9.132 | 29.257 | 578.503 | 90.871 | 68823
PRRTTL61VERTE | LIT 225kV N0 1 PIERRETTE (LA) - VERTEFEUILLE | PIERRETTE (LA) | PRRTT | VERTEFEUILLE | VERTE | 225 | 825 | 825 | 990 | 990 |  |  | 0.951 | 4.24 | 114.525 | 17.99 | 10423
P.HA5L61ROSPE | LIT 225kV N0 1 PLAINE HAUTE-ROSPEZ | PLAINE HAUTE | P.HA5 | ROSPEZ | ROSPE | 225 | 1375 | 1437 | 1437 | 1484 |  |  | 3.275 | 21.742 | 503.205 | 79.043 | 54579
P.HA5L61TREGU | LIT 225kV N0 1 PLAINE HAUTE-TREGUEUX | PLAINE HAUTE | P.HA5 | TREGUEUX | TREGU | 225 | 1212 | 1262 | 1262 | 1318 |  |  | 0.835 | 5.58 | 127.834 | 20.08 | 13973
PLAISL61ROMAI | LIT 225kV N0 1 PLAISANCE-ROMAINVILLE | PLAISANCE | PLAIS | ROMAINVILLE | ROMAI | 225 | 480 | 480 | 835 | 835 |  |  | 0.393 | 2.335 | 1094.318 | 171.895 | 7921
P.ORGL61RQROU | LIT 225kV N0 1 PLAN-D ORGON - ROQUEROUSSE | PLAN-D ORGON | P.ORG | ROQUEROUSSE | RQROU | 225 | 816 | 889 | 889 | 947 |  |  | 1.755 | 8.022 | 176.076 | 27.658 | 19640
P.GASL61SAUS5 | LIT 225kV N0 1 PLESSIS-GASSOT - SAUSSET | PLESSIS-GASSOT | P.GAS | SAUSSET | SAUS5 | 225 | 899 | 984 | 984 | 1061 |  |  | 1.154 | 5.691 | 127.395 | 20.011 | 14028
P.GASL61SEINE | LIT 225kV N0 1 PLESSIS-GASSOT - SEINE | PLESSIS-GASSOT | P.GAS | SEINE | SEINE | 225 | 888 | 950 | 972 | 1049 |  |  | 1.303 | 6.855 | 219.548 | 34.486 | 17062
PTARLL61SAONE | LIT 225kV N0 1 PONTARLIER - SAONE | PONTARLIER | PTARL | SAONE | SAONE | 225 | 412 | 420 | 420 | 420 |  |  | 6.401 | 17.196 | 364.928 | 57.323 | 41663
PONTEL61REALT | LIT 225kV N0 1 PONTEAU - REALTOR | PONTEAU | PONTE | REALTOR | REALT | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.009 | 10.357 | 402.457 | 63.218 | 34309
P.SEPL61SAINN | LIT 225kV N0 1 PONT-SEPT-SAINNEVILLE | PONT-SEPT | P.SEP | SAINNEVILLE | SAINN | 225 | 455 | 455 | 560 | 560 |  |  | 0.62 | 3.468 | 878.004 | 137.916 | 11365
P.SEPL61SANDO | LIT 225kV N0 1 PONT-SEPT-SANDOUVILLE | PONT-SEPT | P.SEP | SANDOUVILLE | SANDO | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.877 | 5.875 | 133.813 | 21.019 | 14613
PORCHL61PUISE | LIT 225kV N0 1 PORCHEVILLE-PUISEUX | PORCHEVILLE | PORCH | PUISEUX | PUISE | 225 | 511 | 768 | 768 | 979 |  |  | 1.381 | 9.031 | 208.143 | 32.695 | 22686
PORCHL61SSBAI | LIT 225kV N0 1 PORCHEVILLE-ST-PIERRE-DE-BAILLEUL | PORCHEVILLE | PORCH | ST-PIERRE-DE-BAILLEUL | SSBAI | 225 | 1140 | 1248 | 1248 | 1347 |  |  | 2.91 | 19.42 | 433.267 | 68.057 | 48359
P.SIML61RIVEN | LIT 225kV N0 1 PORTET-ST-SIMON - RIVENEUVE | PORTET-ST-SIMON | P.SIM | RIVENEUVE | RIVEN | 225 | 813 | 890 | 890 | 966 |  |  | 4.996 | 22.853 | 479.045 | 75.248 | 54760
P.SIML61SSORE | LIT 225kV N0 1 PORTET-ST-SIMON - ST-ORENS | PORTET-ST-SIMON | P.SIM | ST-ORENS | SSORE | 225 | 780 | 780 | 940 | 940 |  |  | 0.722 | 4.696 | 183.566 | 28.834 | 11937
P.SIML61TARAS | LIT 225kV N0 1 PORTET-ST-SIMON -TARASCON | PORTET-ST-SIMON | P.SIM | TARASCON | TARAS | 225 | 430 | 550 | 550 | 630 |  |  | 7.159 | 32.6 | 712.821 | 111.97 | 79654
P.JERL61SANDO | LIT 225kV N0 1 PORT-JEROME-SANDOUVILLE | PORT-JEROME | P.JER | SANDOUVILLE | SANDO | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.336 | 8.951 | 204.159 | 32.069 | 22280
P.JERL61VAUPA | LIT 225kV N0 1 PORT-JEROME-VAUPALIERE (LA) | PORT-JEROME | P.JER | VAUPALIERE (LA) | VAUPA | 225 | 618 | 745 | 745 | 819 |  |  | 3.64 | 16.84 | 441.076 | 61 | 41042
P.ROUL61SQUIV | LIT 225kV N0 1 POTEAU-ROUGE - SQUIVIDAN | POTEAU-ROUGE | P.ROU | SQUIVIDAN | SQUIV | 225 | 1280 | 1332 | 1332 | 1382 |  |  | 3.689 | 24.528 | 565.699 | 88.86 | 61476
P.ROUL61THEIX | LIT 225kV N0 1 POTEAU-ROUGE - THEIX | POTEAU-ROUGE | P.ROU | THEIX | THEIX | 225 | 1212 | 1262 | 1262 | 1318 |  |  | 3.166 | 21.043 | 486.15 | 76.364 | 52773
PRATCL61TREVA | LIT 225kV N0 1 PRATCLAUX - TREVAS | PRATCLAUX | PRATC | TREVAS | TREVA | 225 | 1059 | 1141 | 1141 | 1215 |  |  | 3.554 | 21.054 | 500.752 | 78.658 | 53845
PRATCL61SANSS | LIT 225kV N0 1 PRATCLAUX-SANSSAC (L'EGLISE) | PRATCLAUX | PRATC | SANSSAC (L'EGLISE) | SANSS | 225 | 639 | 717 | 717 | 860 |  |  | 1.338 | 6.033 | 131.644 | 20.679 | 14685
P.ANDL61SAUS2 | LIT 225kV N0 1 PRAZ-ST-ANDRE-SAUSSAZ II (LA) | PRAZ-ST-ANDRE | P.AND | SAUSSAZ II (LA) | SAUS2 | 225 | 966 | 1076 | 1076 | 1168 |  |  | 0.68 | 3.98 | 89.603 | 14 | 9854
PREGUL61SAINT | LIT 225kV N0 1 PREGUILLAC - SAINTES | PREGUILLAC | PREGU | SAINTES | SAINT | 225 | 1180 | 1310 | 1310 | 1390 |  |  | 0.668 | 4.489 | 162.494 | 25.524 | 11329
PRELEL61SEREI | LIT 225kV N0 1 PRELES (LES)-SEREIN | PRELES (LES) | PRELE | SEREIN | SEREI | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 0.842 | 5.611 | 129.112 | 20.281 | 13940
PUSY L61ROLAM | LIT 225kV N0 1 PUSY-ROLAMPONT | PUSY | PUSY | ROLAMPONT | ROLAM | 225 | 827 | 891 | 891 | 976 |  |  | 6.717 | 30.544 | 655.18 | 102.916 | 74096
PYMONL61VOUGL | LIT 225kV N0 1 PYMONT-VOUGLANS | PYMONT | PYMON | VOUGLANS | VOUGL | 225 | 704 | 866 | 866 | 990 |  |  | 2.284 | 14.652 | 344.048 | 54.043 | 37473
Q.SEIL61SAUMA | LIT 225KV N0 1 QUATRE SEIGNEURS - SAUMAD | QUATRE-SEIGNEURS | Q.SEI | SAUMADE | SAUMA | 225 | 1100 | 1100 | 1300 | 1300 |  |  | 0.086 | 1.147 | 2230.8 | 350.413 | 7800
Q.SEIL61TAMAR | LIT 225kV N0 1 QUATRE SEIGNEURS - TAMAREAU | QUATRE-SEIGNEURS | Q.SEI | TAMAREAU | TAMAR | 225 | 855 | 855 | 1040 | 1040 |  |  | 0.684 | 4.549 | 190.626 | 29.943 | 11660
QUINTL61SSCAL | LIT 225kV N0 1 QUINTES (LES)-ST-CALAIS | QUINTES (LES) | QUINT | ST-CALAIS | SSCAL | 225 | 1249 | 1316 | 1316 | 1389 |  |  | 2.354 | 15.737 | 357.959 | 56.228 | 39236
R.TORL61VLEJU | LIT 225kV N0 1 RAIE-TORTUE - VILLEJUST | RAIE-TORTUE | R.TOR | VILLEJUST | VLEJU | 225 | 1040 | 1285 | 1285 | 1388 |  |  | 0.478 | 4.652 | 200.655 | 31.519 | 15924
RASSUL61RQROU | LIT 225kV N0 1 RASSUEN-ROQUEROUSSE | RASSUEN | RASSU | ROQUEROUSSE | RQROU | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.76 | 12.056 | 283.583 | 44.545 | 30192
REALTL61SEPTE | LIT 225kV N0 1 REALTOR-SEPTEMES | REALTOR | REALT | SEPTEMES | SEPTE | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.413 | 2.766 | 63.053 | 9.904 | 6966
RICHEL61SSHUB | LIT 225kV N0 1 RICHEMONT-SAINT HUBERT | RICHEMONT | RICHE | SAINT HUBERT | SSHUB | 225 | 413 | 714 | 714 | 899 |  |  | 0.254 | 1.501 | 34.258 | 5.381 | 3770
RIVENL61TARAS | LIT 225kV N0 1 RIVENEUVE-TARASCON | RIVENEUVE | RIVEN | TARASCON | TARAS | 225 | 716 | 807 | 807 | 887 |  |  | 3.286 | 14.921 | 315.716 | 49.593 | 35577
RIVIEL61SANSS | LIT 225kV N0 1 RIVIERE (LA) - SANSSAC (L'EGLISE) | RIVIERE (LA) | RIVIE | SANSSAC (L'EGLISE) | SANSS | 225 | 900 | 900 | 1100 | 1100 |  |  | 4.186 | 25.175 | 2476.869 | 389.066 | 69448
RIVIEL61TREVA | LIT 225kV N0 1 RIVIERE (LA)-TREVAS | RIVIERE (LA) | RIVIE | TREVAS | TREVA | 225 | 639 | 717 | 717 | 783 |  |  | 2.465 | 11.382 | 235.438 | 36.983 | 27117
ROGNAL61RQROU | LIT 225kV N0 1 ROGNAC-ROQUEROUSSE | ROGNAC | ROGNA | ROQUEROUSSE | RQROU | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.492 | 10.006 | 227.329 | 34.872 | 24566
ROGNAL61SSCHA | LIT 225kV N0 1 ROGNAC-ST-CHAMAS | ROGNAC | ROGNA | ST-CHAMAS | SSCHA | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.848 | 5.624 | 130.279 | 20.464 | 14043
ROMAIL61VLEVA | LIT 225kV N0 1 ROMAINVILLE-VILLEVAUDE | ROMAINVILLE | ROMAI | VILLEVAUDE | VLEVA | 225 | 480 | 480 | 782 | 835 |  |  | 1.394 | 7.184 | 1176.89 | 184.865 | 20202
RQROUL61SSEST | LIT 225kV N0 1 ROQUEROUSSE-ST-ESTEVE | ROQUEROUSSE | RQROU | ST-ESTEVE | SSEST | 225 | 1034 | 1128 | 1128 | 1203 |  |  | 1.439 | 9.427 | 209.387 | 32.89 | 23308
ROUGEL61YAINV | LIT 225kV N0 1 ROUGEMONTIER-YAINVILLE | ROUGEMONTIER | ROUGE | YAINVILLE | YAINV | 225 | 757 | 946 | 946 | 1075 |  |  | 1.618 | 10.872 | 243.916 | 38.314 | 26893
ROUSSL61SEREI | LIT 225kV N0 1 ROUSSON-SEREIN | ROUSSON | ROUSS | SEREIN | SEREI | 225 | 435 | 595 | 595 | 680 |  |  | 3.821 | 17.297 | 381.742 | 59.964 | 42580
RUEYRL61SAVIG | LIT 225kV N0 1 RUEYRES-SAVIGNAC | RUEYRES | RUEYR | SAVIGNAC | SAVIG | 225 | 548 | 606 | 606 | 678 |  |  | 5.109 | 19.887 | 399.14 | 62.697 | 45790
SACL5L61VLERA | LIT 225KV N0 1 SACLAY (PLATEAU) - VILLER | SACLAY (PLATEAU) | SACL5 | VILLERAS | VLERA | 225 | [6 empty] | 0.171 | 0.865 | 1025.703 | 161.117 | 5103
SAINNL61YAINV | LIT 225kV N0 1 SAINNEVILLE-YAINVILLE | SAINNEVILLE | SAINN | YAINVILLE | YAINV | 225 | 769 | 872 | 872 | 961 |  |  | 4.38 | 19.966 | 456.298 | 71.675 | 49270
SANILL61TUILI | LIT 225kV N0 1 SANILHAC-TUILIERES | SANILHAC | SANIL | TUILIERES | TUILI | 225 | 289 | 543 | 543 | 682 |  |  | 4.218 | 19.176 | 417.052 | 65.51 | 46667
SAUS5L61VLEVA | LIT 225kV N0 1 SAUSSET-VILLEVAUDE | SAUSSET | SAUS5 | VILLEVAUDE | VLEVA | 225 | 750 | 850 | 850 | 895 |  |  | 0.985 | 4.45 | 98.876 | 15.531 | 11001
S.GUYL61ZFONC | LIT 225kV N0 1 SAUVETERRE-DE-GUYENNE - PIQUAGE A FONCROSE | SAUVETERRE-DE-GUYENNE | S.GUY |  | ZFONC | 225 | 85 | 85 | 85 | 85 |  |  | 0.041 | 0.125 | 114.859 | 18.042 | 700
SEREIL61TONNE | LIT 225kV N0 1 SEREIN-TONNERRE | SEREIN | SEREI | TONNERRE | TONNE | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 1.393 | 9.486 | 208.784 | 32.796 | 23150
S.PONL61SISTE | LIT 225kV N0 1 SERRE-PONCON-SISTERON | SERRE-PONCON | S.PON | SISTERON | SISTE | 225 | 862 | 928 | 928 | 987 |  |  | 3.508 | 16.913 | 380.908 | 59.833 | 42224
SERRIL61SSV.E | LIT 225kV N0 1 SERRIERES-ST-VULBAS-EST | SERRIERES | SERRI | ST-VULBAS-EST | SSV.E | 225 | 204 | 397 | 397 | 493 |  |  | 6.685 | 21.696 | 425.839 | 66.891 | 50471
SOLEIL61VOLVO | LIT 225kV N0 1 SOLEIL (LE)-VOLVON | SOLEIL (LE) | SOLEI | VOLVON | VOLVO | 225 | 1123 | 1211 | 1211 | 1290 |  |  | 0.897 | 5.987 | 137.226 | 21.555 | 14948
SSCESL61SSCHR | LIT 225kV N0 1 ST CESAIRE - ST CHRISTOL | ST-CESAIRE | SSCES | ST-CHRISTOL | SSCHR | 225 | 597 | 676 | 676 | 724 |  |  | 3.42 | 11.744 | 229.221 | 36.006 | 27156
SSAUBL61SSTUL | LIT 225kV N0 1 ST-AUBAN-STE-TULLE | ST-AUBAN | SSAUB | STE-TULLE | SSTUL | 225 | 1123 | 1201 | 1201 | 1268 |  |  | 5.042 | 18.112 | 359.656 | 56.495 | 42091
SSAU5L61VERSA | LIT 225kV N0 1 ST-AUBIN-VERSAILLES | ST-AUBIN | SSAU5 | VERSAILLES | VERSA | 225 | 673 | 673 | 826 | 826 |  |  | 0.412 | 1.313 | 2021.064 | 317.468 | 10815
SSAVOL61VIGY | LIT 225kV N0 1 ST-AVOLD-VIGY | ST-AVOLD | SSAVO |  | 1VIGY | 225 | 1412 | 1412 | 1639 | 1639 |  |  | 0.723 | 9.937 | 473.742 | 74.415 | 32825
SSELOL61VNOL | LIT 225kV N0 1 ST-ELOI - VIGNOL | ST-ELOI | SSELO |  | 1VNOL | 225 | 617 | 740 | 740 | 826 |  |  | 5.403 | 26.383 | 566.256 | 88.947 | 63891
SSESTL61SSTUL | LIT 225kV N0 1 ST-ESTEVE-SAINTE-TULLE 1 | ST-ESTEVE | SSEST | STE-TULLE | SSTUL | 225 | 280 | 647 | 647 | 824 |  |  | 1.993 | 13.509 | 318.753 | 50.07 | 34371
SSJULL61VIGY | LIT 225kV N0 1 ST-JULIEN-VIGY | ST-JULIEN | SSJUL |  | 1VIGY | 225 | 1100 | 1187 | 1187 | 1302 |  |  | 0.433 | 2.901 | 66.124 | 10.387 | 7202
SSOREL61VERFE | LIT 225kV N0 1 ST-ORENS-VERFEIL | ST-ORENS | SSORE | VERFEIL | VERFE | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 1.057 | 7.079 | 161.471 | 25.364 | 17610
TAVELL61VIRAD | LIT 225kV N0 1 TAVEL - VIRADEL | TAVEL | TAVEL | VIRADEL | VIRAD | 225 | 985 | 985 | 1129 | 1165 |  |  | 2.891 | 18.245 | 553.344 | 86.919 | 46486
VAUPAL61YAINV | LIT 225kV N0 1 VAUPALIERE (LA)-YAINVILLE | VAUPALIERE (LA) | VAUPA | YAINVILLE | YAINV | 225 | 599 | 746 | 746 | 847 |  |  | 1.433 | 6.577 | 188.427 | 29.598 | 16018
VERTEL61WEPPE | LIT 225kV N0 1 VERTEFEUILLE-WEPPES | VERTEFEUILLE | VERTE | WEPPES | WEPPE | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.758 | 5.074 | 115.966 | 18.216 | 12642
VINCEL61VITTE | LIT 225kV N0 1 VINCEY-VITTEL | VINCEY | VINCE | VITTEL | VITTE | 225 | 881 | 964 | 964 | 1040 |  |  | 2.119 | 14.104 | 324.295 | 50.94 | 35257
ALLINL62CORNI | LIT 225kV N0 2 ALLINGES-CORNIER | ALLINGES | ALLIN | CORNIER | CORNI | 225 | 966 | 1076 | 1076 | 1168 |  |  | 2.42 | 14.474 | 343.942 | 54.026 | 36992
AQUEDL62CIROL | LIT 225kV N0 2 AQUEDUCS (LES)-CIROLLIERS | AQUEDUCS (LES) | AQUED | CIROLLIERS | CIROL | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.551 | 3.674 | 84.388 | 13.256 | 9206
ARDOIL62TAVEL | LIT 225kV N0 2 ARDOISE (L )-TAVEL | ARDOISE (L ) | ARDOI | TAVEL | TAVEL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.649 | 4.346 | 99.257 | 15.591 | 10815
ARGIAL62MOUGU | LIT 225kV N0 2 ARGIA (BAYONNE SUD)-MOUGUERRE | ARGIA (BAYONNE SUD) | ARGIA | MOUGUERRE | MOUGU | 225 | 635 | 635 | 870 | 870 |  |  | 0.382 | 2.65 | 571.547 | 89.778 | 7966
ARNAGL62QUINT | LIT 225kV N0 2 ARNAGE-QUINTES (LES) | ARNAGE | ARNAG | QUINTES (LES) | QUINT | 225 | 1032 | 1124 | 1124 | 1212 |  |  | 0.328 | 2.216 | 52.246 | 8.207 | 5558
ARRIGL62CHARE | LIT 225kV N0 2 ARRIGHI-CHARENTON | ARRIGHI | ARRIG | CHARENTON | CHARE | 225 | 220 | 220 | 340 | 340 |  |  | 0.139 | 0.473 | 1310.806 | 205.901 | 4473
ARRIGL62MORBR | LIT 225kV N0 2 ARRIGHI-MORBRAS | ARRIGHI | ARRIG | MORBRAS | MORBR | 225 | 1980 | 2008 | 2250 | 2420 |  |  | 0.665 | 6.133 | 423.756 | 66.563 | 22198
BALMAL62VERFE | LIT 225kV N0 2 BALMA (POSTE)-VERFEIL | BALMA (POSTE) | BALMA | VERFEIL | VERFE | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 0.944 | 6.329 | 144.256 | 22.66 | 15741
B.MONL62GAMPA | LIT 225kV N0 2 BEAUMONT-MONTEUX-GAMPALOUP | BEAUMONT-MONTEUX | B.MON | GAMPALOUP | GAMPA | 225 | 880 | 992 | 992 | 1086 |  |  | 2.17 | 14.7 | 331.537 | 52 | 36312
BXTO5L62LATEN | LIT 225kV N0 2 BEAUTOR (POSTE)-LATENA | BEAUTOR (POSTE) | BXTO5 | LATENA | LATEN | 225 | 1400 | 1500 | 1500 | 1550 |  |  | 0.95 | 9.241 | 399.141 | 62.697 | 31657
BEC5 L62MQIS | LIT 225KV N0 2 BEC - MARQUIS (LE) | BEC | BEC5 | MARQUIS (LE) | MQIS | 225 | [6 empty] | 0.267 | 1.165 | 126.265 | 19.834 | 4807
BEZAUL62VANDI | LIT 225kV N0 2 BEZAUMONT-VANDIERES | BEZAUMONT | BEZAU | VANDIERES | VANDI | 225 | 1172 | 1285 | 1285 | 1375 |  |  | 0.817 | 5.428 | 125.4 | 19.698 | 13741
BEZ.EL62SSVIN | LIT 225KV N0 2 BEZIERS-EST - ST-VINCENT | BEZIERS-EST | BEZ.E | ST-VINCENT | SSVIN | 225 | [6 empty] | 0.259 | 0.761 | 729.029 | 114.516 | 4443
BOISSL62CUS.P | LIT 225kV N0 2 BOISSE (LA) - CUSSET-POSTE | BOISSE (LA) | BOISS | CUSSET-POSTE | CUS.P | 225 | 857 | 857 | 1024 | 1024 |  |  | 0.63 | 4.83 | 262.516 | 40 | 12768
BOISSL62MIONS | LIT 225kV N0 2 BOISSE (LA) - MIONS | BOISSE (LA) | BOISS | MIONS | MIONS | 225 | 900 | 1015 | 1015 | 1112 |  |  | 1.16 | 8.01 | 265.136 | 39 | 20131
BOLL5L62TRI.P | LIT 225kV N0 2 BOLLENE - TRICASTIN-POSTE (LE) | BOLLENE (POSTE RESEAU) | BOLL5 | TRICASTIN-POSTE (LE) | TRI.P | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.344 | 2.304 | 52.401 | 8.231 | 5733
BONN6L62VALDI | LIT 225kV N0 2 BONNEAU-VALDIVIENNE | BONNEAU | BONN6 | VALDIVIENNE | VALDI | 225 | 1180 | 1310 | 1310 | 1390 |  |  | 1.653 | 10.436 | 269.252 | 42.294 | 27592
B.CARL62LINGO | LIT 225kV N0 2 BROC-CARROS (LE) - LINGOSTIERE | BROC-CARROS (LE) | B.CAR | LINGOSTIERE | LINGO | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.715 | 4.787 | 109.367 | 17.179 | 11928
B.CARL62T.VIC | LIT 225kV N0 2 BROC-CARROS (LE) - TRINITE-VICTOR | BROC-CARROS (LE) | B.CAR | TRINITE-VICTOR | T.VIC | 225 | 1062 | 1081 | 1160 | 1207 |  |  | 0.812 | 5.544 | 128.413 | 20.171 | 13937
CANTEL62NAOUT | LIT 225kV N0 2 CANTEGRIT-NAOUTOT | CANTEGRIT | CANTE | NAOUTOT | NAOUT | 225 | 845 | 925 | 925 | 1005 |  |  | 2.188 | 14.696 | 330.222 | 51.871 | 36790
CARRIL62TERRI | LIT 225kV N0 2 CARRIERES-TERRIER | CARRIERES | CARRI | TERRIER | TERRI | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 0.454 | 4.265 | 196.105 | 30.804 | 15648
CAZARL62LANNE | LIT 225kV N0 2 CAZARIL-LANNEMEZAN | CAZARIL | CAZAR | LANNEMEZAN | LANNE | 225 | 1018 | 1117 | 1117 | 1213 |  |  | 0.776 | 4.67 | 108.209 | 16.997 | 11751
CERNAL62VESLE | LIT 225kV N0 2 CERNAY-VESLE | CERNAY | CERNA | VESLE | VESLE | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 1.051 | 7.006 | 161.172 | 25.317 | 17550
CHAINL62DAMBR | LIT 225kV N0 2 CHAINGY - DAMBRON | CHAINGY | CHAIN | DAMBRON | DAMBR | 225 | 888 | 983 | 983 | 1042 |  |  | 2.522 | 11.141 | 225.767 | 35.463 | 26253
CHALOL62GROSN | LIT 225kV N0 2 CHALON-GROSNE | CHALON | CHALO | GROSNE | GROSN | 225 | 1400 | 1500 | 1500 | 1550 |  |  | 0.752 | 7.047 | 327.043 | 51.372 | 25070
CPNIEL62EYBEN | LIT 225kV N0 2 CHAMPAGNIER - EYBENS | CHAMPAGNIER | CPNIE | EYBENS | EYBEN | 225 | 1014 | 1014 | 1178 | 1191 |  |  | 0.517 | 3.368 | 77.833 | 12.226 | 8569
C.REGL62VIELM | LIT 225kV N0 2 CHAMPS-REGNAUD-VIELMOULIN | CHAMPS-REGNAUD | C.REG | VIELMOULIN | VIELM | 225 | 847 | 865 | 985 | 1060 |  |  | 2.005 | 13.363 | 336.523 | 52.861 | 33800
CHAN6L62REVIG | LIT 225kV N0 2 CHANCENAY-REVIGNY | CHANCENAY | CHAN6 | REVIGNY | REVIG | 225 | 1172 | 1285 | 1285 | 1375 |  |  | 0.977 | 6.515 | 149.893 | 23.545 | 16240
C.GOML62E.BOT | LIT 225kV N0 2 CHATEAU-GOMBERT - ENCO-DE-BOTTE | CHATEAU-GOMBERT | C.GOM | ENCO-DE-BOTTE | E.BOT | 225 | 438 | 438 | 438 | 438 |  |  | 0.337 | 1.122 | 1092.959 | 171.682 | 6355
C.RHOL62L.NEU | LIT 225kV N0 2 CHATEAUNEUF-DU-RHONE-LOGIS-NEUF | CHATEAUNEUF-DU-RHONE | C.RHO | LOGIS-NEUF | L.NEU | 225 | 862 | 928 | 928 | 987 |  |  | 2.742 | 12.439 | 293.511 | 46.105 | 30035
CHESNL62CZTRY | LIT 225kV N0 2 CHESNOY (LE)-COURTRY | CHESNOY (LE) | CHESN | COURTRY | CZTRY | 225 | 920 | 920 | 1100 | 1100 |  |  | 1.181 | 7.961 | 285.225 | 44.803 | 20002
CHOLEL62DISTR | LIT 225kV N0 2 CHOLET-DISTRE | CHOLET | CHOLE | DISTRE | DISTR | 225 | 957 | 1023 | 1023 | 1096 |  |  | 7.299 | 36.334 | 812.439 | 127.618 | 89929
CHOO5L62MAZUR | LIT 225kV N0 2 CHOOZ-MAZURES | CHOOZ | CHOO5 | MAZURES | MAZUR | 225 | 843 | 909 | 909 | 996 |  |  | 0.759 | 9.395 | 351.923 | 55.28 | 29849
CIROLL62LOGES | LIT 225kV N0 2 CIROLLIERS - LOGES (LES) | CIROLLIERS | CIROL | LOGES (LES) | LOGES | 225 | 880 | 880 | 1130 | 1130 |  |  | 0.377 | 2.555 | 221.677 | 34.821 | 7205
CLEONL62G.COU | LIT 225kV N0 2 CLEON-GRAND-COURONNE | CLEON | CLEON | GRAND-COURONNE | G.COU | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.329 | 2.198 | 50.342 | 7.908 | 5473
COQUAL62ROUGE | LIT 225kV N0 2 COQUAINVILLIERS-ROUGEMONTIER | COQUAINVILLIERS | COQUA | ROUGEMONTIER | ROUGE | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 2.765 | 18.62 | 419.3 | 65.864 | 46234
CORBIL62DISTR | LIT 225kV N0 2 CORBIERE (LA)-DISTRE | CORBIERE (LA) | CORBI | DISTRE | DISTR | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 2.745 | 18.496 | 416.468 | 65.419 | 45808
COR.PL62PTCHA | LIT 225kV N0 2 CORDEMAIS-POSTE-PONTCHATEAU | CORDEMAIS-POSTE | COR.P | PONTCHATEAU | PTCHA | 225 | 1249 | 1337 | 1337 | 1432 |  |  | 1.421 | 9.618 | 226.939 | 35.648 | 24461
CORNIL62GEN.P | LIT 225kV N0 2 CORNIER-GENISSIAT-POSTE | CORNIER | CORNI | GENISSIAT-POSTE | GEN.P | 225 | 396 | 660 | 660 | 830 |  |  | 2.437 | 15.786 | 363.53 | 57.103 | 39423
COUDOL62NEOUL | LIT 225kV N0 2 COUDON (LE)-NEOULES | COUDON (LE) | COUDO | NEOULES | NEOUL | 225 | 1001 | 1093 | 1093 | 1165 |  |  | 1.096 | 6.601 | 152.605 | 23.971 | 16604
CREC6L62WEPPE | LIT 225kV N0 2 CRECHETS (LES)-WEPPES | CRECHETS (LES) | CREC6 | WEPPES | WEPPE | 225 | 810 | 810 | 945 | 945 |  |  | 0.872 | 5.815 | 182.319 | 28.639 | 14426
DARSEL62FEUIL | LIT 225kV N0 2 DARSE-FEUILLANE | DARSE | DARSE | FEUILLANE | FEUIL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.725 | 4.838 | 140.51 | 22.071 | 13766
DRONNL62TOURB | LIT 225kV N0 2 DRONNIERE (LA) - TOURBE | DRONNIERE (LA) | DRONN | TOURBE | TOURB | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.615 | 4.098 | 94.285 | 14.81 | 10550
ECHALL62GIVOR | LIT 225kV N0 2 ECHALAS - GIVORS | ECHALAS | ECHAL | GIVORS | GIVOR | 225 | 900 | 910 | 1015 | 1080 |  |  | 0.42 | 2.89 | 140.056 | 22 | 7034
E.BOTL62PALUN | LIT 225kV N0 2 ENCO-DE-BOTTE-PALUN (LA) | ENCO-DE-BOTTE | E.BOT | PALUN (LA) | PALUN | 225 | 1001 | 1093 | 1093 | 1165 |  |  | 1.123 | 7.058 | 164.112 | 25.779 | 17816
FALLOL62ZV.BE | LIT 225kV N0 2 FALLOU -PIQUAGE A VILLIERS-LE-BEL | FALLOU | FALLO |  | ZV.BE | 225 | 930 | 930 | 1050 | 1050 |  |  | 0.934 | 6.191 | 263.955 | 41.462 | 16184
FALLOL62NOVIO | LIT 225kV N0 2 FALLOU-NOVION | FALLOU | FALLO | NOVION | NOVIO | 225 | 935 | 935 | 1105 | 1105 |  |  | 0.106 | 0.916 | 1140.517 | 179.152 | 5478
FEUILL62PONTE | LIT 225kV N0 2 FEUILLANE - PONTEAU | FEUILLANE | FEUIL | PONTEAU | PONTE | 225 | 835 | 835 | 913 | 913 |  |  | 0.555 | 5.856 | 227.309 | 35.706 | 19037
FOUSCL62TAMAR | LIT 225kV N0 2 FOUSCAIS - TAMAREAU | FOUSCAIS | FOUSC | TAMAREAU | TAMAR | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.495 | 9.985 | 228.591 | 35.907 | 24908
FREJUL62TRANS | LIT 225kV N0 2 FREJUS-TRANS | FREJUS | FREJU | TRANS | TRANS | 225 | 1062 | 1066 | 1160 | 1238 |  |  | 1.397 | 9.218 | 305.184 | 47.938 | 22800
GINESL62LESQU | LIT 225kV N0 2 GINESTOUS-LESQUIVE | GINESTOUS | GINES | LESQUIVE | LESQU | 225 | 1080 | 1185 | 1185 | 1289 |  |  | 1.644 | 11.017 | 251.258 | 39.467 | 27386
G.BANL62GIVOR | LIT 225kV N0 2 GIVORS-BANS-GIVORS | GIVORS-BANS | G.BAN | GIVORS | GIVOR | 225 | 468 | 722 | 722 | 899 |  |  | 0.03 | 0.2 | 5.108 | 0 | 500
GIVORL62MIONS | LIT 225kV N0 2 GIVORS-MIONS | GIVORS | GIVOR | MIONS | MIONS | 225 | 576 | 917 | 917 | 1260 |  |  | 0.668 | 6.62 | 240.312 | 37.748 | 20765
GIVORL62SOLEI | LIT 225kV N0 2 GIVORS-SOLEIL (LE) | GIVORS | GIVOR | SOLEIL (LE) | SOLEI | 225 | 639 | 717 | 717 | 783 |  |  | 2.802 | 13.691 | 395.942 | 62.194 | 34932
G.COUL62ROUGE | LIT 225kV N0 2 GRAND-COURONNE-ROUGEMONTIER | GRAND-COURONNE | G.COU | ROUGEMONTIER | ROUGE | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.43 | 9.58 | 218.688 | 34.351 | 23822
G.COUL62SSROU | LIT 225kV N0 2 GRAND-COURONNE-ST ETIENNE DU ROUVRAY | GRAND-COURONNE | G.COU | ST ETIENNE DU ROUVRAY | SSROU | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.544 | 3.646 | 83.153 | 13.062 | 9071
G.COUL62VAUPA | LIT 225kV N0 2 GRAND-COURONNE-VAUPALIERE (LA) | GRAND-COURONNE | G.COU | VAUPALIERE (LA) | VAUPA | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 1.53 | 10.18 | 236.753 | 36.6 | 25444
G.SYNL62WARAN | LIT 225kV N0 2 GRANDE-SYNTHE-WARANDE | GRANDE-SYNTHE | G.SYN | RANDENS | RANDE | 225 | 1250 | 1250 | 1250 | 1250 |  |  | 0.884 | 5.893 | 135.453 | 21.277 | 14713
GRANZL62SSFLO | LIT 225kV N0 2 GRANZAY - ST-FLORENT | GRANZAY | GRANZ | ST-FLORENT | SSFLO | 225 | 1012 | 1150 | 1150 | 1247 |  |  | 0.645 | 4.296 | 98.871 | 15.531 | 10767
GRIM5L62TRANS | LIT 225KV N0 2 GRIMAUD - TRANS | GRIMAUD | GRIM5 | TRANS | TRANS | 225 | [6 empty] | 1.682 | 11.13 | 986.374 | 154.939 | 29772
G.CAIL62VALEN | LIT 225kV N0 2 GROS-CAILLOU - VALENCIENNES | GROS-CAILLOU | G.CAI | VALENCIENNES | VALEN | 225 | 915 | 915 | 1030 | 1075 |  |  | 1.618 | 8.259 | 241.119 | 37.875 | 20829
G.CAIL62MASTA | LIT 225kV N0 2 GROS-CAILLOU-MASTAING | GROS-CAILLOU | G.CAI | MASTAING | MASTA | 225 | 1273 | 1346 | 1346 | 1453 |  |  | 0.259 | 1.72 | 39.833 | 6.257 | 4318
HARC7L62R.TOR | LIT 225kV N0 2 HARCOURT (POSTE BLINDE)-RAIE-TORTUE | HARCOURT (POSTE BLINDE) | HARC7 | RAIE-TORTUE | R.TOR | 225 | 660 | 660 | 900 | 900 |  |  | 0.218 | 0.842 | 2106.11 | 330.827 | 6253
HAVR5L62P.SEP | LIT 225kV N0 2 HAVRE (LE) (POSTE) - PONT-SEPT | HAVRE (LE) (POSTE) | HAVR5 | PONT-SEPT | P.SEP | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 0.127 | 1.241 | 53.348 | 8.38 | 4244
HOLQUL62LONG9 | LIT 225kV N0 2 HOLQUE-LONGUENESSE | HOLQUE | HOLQU | LONGUENESSE | LONG9 | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.779 | 5.192 | 119.427 | 18.76 | 12948
JONQUL62SSCES | LIT 225kV N0 2 JONQUIERES-ST-CESAIRE | JONQUIERES | JONQU | ST-CESAIRE | SSCES | 225 | 990 | 990 | 1165 | 1165 |  |  | 1.302 | 8.682 | 255.299 | 40.102 | 21840
GAUDIL62MOREA | LIT 225kV N0 2 LA GAUDIERE - MOREAU | GAUDIERE (LA) | GAUDI | MOREAU | MOREA | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 1.46 | 9.683 | 224.323 | 35.237 | 24293
LANDEL62MARTY | LIT 225kV N0 2 LANDERNEAU-MARTYRE (LA) | LANDERNEAU | LANDE | MARTYRE (LA) | MARTY | 225 | 1056 | 1123 | 1123 | 1189 |  |  | 0.249 | 1.483 | 35.002 | 5.498 | 3831
LESCAL62MARSI | LIT 225kV N0 2 LESCAR-MARSILLON | LESCAR | LESCA | MARSILLON | MARSI | 225 | 1172 | 1248 | 1248 | 1310 |  |  | 1.085 | 7.269 | 165.72 | 26.031 | 18078
LESQUL62VERLH | LIT 225kV N0 2 LESQUIVE-VERLHAGUET | LESQUIVE | LESQU | VERLHAGUET | VERLH | 225 | 813 | 890 | 890 | 966 |  |  | 2.266 | 10.706 | 226.49 | 35.577 | 25755
LUMESL62MAZUR | LIT 225kV N0 2 LUMES-MAZURES | LUMES | LUMES | MAZURES | MAZUR | 225 | 843 | 909 | 909 | 996 |  |  | 1.832 | 8.917 | 198.64 | 31.202 | 22765
LUTTEL62SIERE | LIT 225kV N0 2 LUTTERBACH-SIERENTZ | LUTTERBACH | LUTTE | SIERENTZ | SIERE | 225 | 847 | 985 | 985 | 1116 |  |  | 1.375 | 9.208 | 210.171 | 33.014 | 22900
MALINL62RULHA | LIT 225kV N0 2 MALINTRAT-RULHAT | MALINTRAT | MALIN | RULHAT | RULHA | 225 | 1034 | 1149 | 1149 | 1244 |  |  | 0.357 | 2.344 | 52.237 | 8.205 | 5787
MAMBEL62PALEN | LIT 225kV N0 2 MAMBELIN-PALENTE | MAMBELIN | MAMBE | PALENTE | PALEN | 225 | 577 | 706 | 706 | 807 |  |  | 3.632 | 21.629 | 470.355 | 73.883 | 52770
MERLAL62SOULL | LIT 225kV N0 2 MERLATIERE - SOULLANS | MERLATIERE | MERLA | SOULLANS | SOULL | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 2.6 | 17.383 | 398.247 | 62.557 | 43412
MEZE5L62PORCH | LIT 225kV N0 2 MEZEROLLES - PORCHEVILLE | MEZEROLLES | MEZE5 | PORCHEVILLE | PORCH | 225 | 520 | 782 | 782 | 998 |  |  | 0.371 | 2.447 | 56.334 | 8.849 | 6134
MIONSL62VENIS | LIT 225kV N0 2 MIONS - VENISSIEUX | MIONS | MIONS | VENISSIEUX | VENIS | 225 | 1050 | 1050 | 1270 | 1270 |  |  | 0.32 | 2.83 | 341.228 | 47 | 9493
MIONSL62MOUCH | LIT 225kV N0 2 MIONS-MOUCHE (LA) | MIONS | MIONS | MOUCHE (LA) | MOUCH | 225 | 1800 | 1940 | 2030 | 2224 |  |  | 0.44 | 4.31 | 293.221 | 27 | 13921
MOLE L62RUEYR | LIT 225kV N0 2 MOLE (LA)-RUEYRES | MOLE (LA) | MOLE | RUEYRES | RUEYR | 225 | 622 | 748 | 748 | 834 |  |  | 6.805 | 32.206 | 666.385 | 104.676 | 77606
MTGROL62PRATC | LIT 225KV N0 2 MONTGROS - PRATCLAUX | MONTGROS | MTGRO | PRATCLAUX | PRATC | 225 | [6 empty] | 3.186 | 9.413 | 406.821 | 63.903 | 22582
MTPELL62TAMAR | LIT 225kV N0 2 MONTPELLIER - TAMAREAU | MONTPELLIER | MTPEL | TAMAREAU | TAMAR | 225 | 1161 | 1241 | 1241 | 1306 |  |  | 1.309 | 8.029 | 188.617 | 29.628 | 20170
MOUL8L62VLEJU | LIT 225kV N0 2 MOULINEAUX-VILLEJUST | MOULINEAUX | MOUL8 | VILLEJUST | VLEJU | 225 | 750 | 750 | 1030 | 1030 |  |  | 0.567 | 5.322 | 1079.904 | 169.631 | 20703
PALUNL62SEPTE | LIT 225kV N0 2 PALUN (LA)-SEPTEMES | PALUN (LA) | PALUN | SEPTEMES | SEPTE | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.911 | 6.115 | 139.176 | 21.862 | 15600
PESSAL62SAUCA | LIT 225kV N0 2 PESSAC-SAUCATS | PESSAC | PESSA | SAUCATS | SAUCA | 225 | 932 | 1049 | 1049 | 1126 |  |  | 1.235 | 8.334 | 201.575 | 31.663 | 21233
P.HA5L62TREGU | LIT 225kV N0 2 PLAINE HAUTE-TREGUEUX | PLAINE HAUTE | P.HA5 | TREGUEUX | TREGU | 225 | 1280 | 1332 | 1332 | 1382 |  |  | 0.837 | 5.591 | 128.092 | 20.121 | 13946
P.GASL62V.BEL | LIT 225kV N0 2 PLESSIS-GASSOT - VILLIERS-LE-BEL | PLESSIS-GASSOT | P.GAS | VILLIERS-LE-BEL | V.BEL | 225 | 520 | 782 | 782 | 998 |  |  | 0.191 | 1.278 | 29.255 | 4.595 | 3259
P.GASL62ZV.BE | LIT 225kV N0 2 PLESSIS-GASSOT -PIQUAGE A VILLIERS-LE-BEL | PLESSIS-GASSOT | P.GAS |  | ZV.BE | 225 | 948 | 1086 | 1086 | 1211 |  |  | 0.191 | 1.278 | 29.034 | 4.561 | 3185
PONTEL62REALT | LIT 225kV N0 2 PONTEAU - REALTOR | PONTEAU | PONTE | REALTOR | REALT | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 1.009 | 10.364 | 402.693 | 63.255 | 34309
P.SIML62VERFE | LIT 225kV N0 2 PORTET-ST-SIMON - VERFEIL | PORTET-ST-SIMON | P.SIM | VERFEIL | VERFE | 225 | 780 | 780 | 940 | 940 |  |  | 1.773 | 11.735 | 344.193 | 54.066 | 29255
PRELEL62SEREI | LIT 225kV N0 2 PRELES (LES)-SEREIN | PRELES (LES) | PRELE | SEREIN | SEREI | 225 | 843 | 909 | 909 | 996 |  |  | 1.266 | 5.727 | 127.06 | 19.959 | 14135
PRIMEL62SAUS5 | LIT 225kV N0 2 PRIMEVERES - SAUSSET | PRIMEVERES | PRIME | SAUSSET | SAUS5 | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.467 | 3.125 | 71.433 | 11.221 | 7790
R.TORL62VLEJU | LIT 225kV N0 2 RAIE-TORTUE-VILLEJUST | RAIE-TORTUE | R.TOR | VILLEJUST | VLEJU | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.453 | 4.383 | 190.948 | 29.994 | 15219
ROMAIL62VLEVA | LIT 225kV N0 2 ROMAINVILLE-VILLEVAUDE | ROMAINVILLE | ROMAI | VILLEVAUDE | VLEVA | 225 | 480 | 480 | 835 | 835 |  |  | 1.252 | 6.998 | 1105.248 | 173.612 | 19154
SOLEIL62VOLVO | LIT 225kV N0 2 SOLEIL (LE)-VOLVON | SOLEIL (LE) | SOLEI | VOLVON | VOLVO | 225 | 981 | 1085 | 1085 | 1176 |  |  | 0.891 | 5.957 | 136.442 | 21.432 | 14858
TAVELL62VIRAD | LIT 225kV N0 2 TAVEL - VIRADEL | TAVEL | TAVEL | VIRADEL | VIRAD | 225 | 985 | 985 | 1129 | 1165 |  |  | 2.908 | 18.35 | 628.419 | 98.712 | 46832
AQUEDL63CIROL | LIT 225kV N0 3 AQUEDUCS (LES) - CIROLLIERS | AQUEDUCS (LES) | AQUED | CIROLLIERS | CIROL | 225 | 1172 | 1285 | 1285 | 1388 |  |  | 0.552 | 3.677 | 84.646 | 13.296 | 9219
ARDOIL63TAVEL | LIT 225kV N0 3 ARDOISE (L ) - TAVEL | ARDOISE (L ) | ARDOI | TAVEL | TAVEL | 225 | 1233 | 1320 | 1320 | 1389 |  |  | 0.648 | 4.319 | 98.958 | 15.544 | 10612
BXTO5L63LATEN | LIT 225kV N0 3 BEAUTOR (POSTE)-LATENA | BEAUTOR (POSTE) | BXTO5 | LATENA | LATEN | 225 | 2200 | 2300 | 2300 | 2400 |  |  | 0.944 | 8.865 | 408.417 | 64.154 | 31467
CAZARL63LANNE | LIT 225kV N0 3 CAZARIL-LANNEMEZAN | CAZARIL | CAZAR | LANNEMEZAN | LANNE | 225 | 1018 | 1117 | 1117 | 1213 |  |  | 0.786 | 4.732 | 109.587 | 17.214 | 11752
CHAINL63DAMBR | LIT 225kV N0 3 CHAINGY-DAMBRON | CHAINGY | CHAIN | DAMBRON | DAMBR | 225 | 1099 | 1099 | 1264 | 1264 |  |  | 1.577 | 10.534 | 315.917 | 49.624 | 26624
CHESNL63CZTRY | LIT 225kV N0 3 CHESNOY (LE)-COURTRY | CHESNOY (LE) | CHESN | COURTRY | CZTRY | 225 | 890 | 890 | 1130 | 1130 |  |  | 1.17 | 7.98 | 179.581 | 43 | 20002
CORBIL61DISTR | LIT 225kV N0 3 CORBIERE (LA)-DISTRE | CORBIERE (LA) | CORBI | DISTRE | DISTR | 225 | 1249 | 1337 | 1337 | 1434 |  |  | 2.745 | 18.499 | 416.532 | 65.429 | 45814
G.BANL63GIVOR | LIT 225kV N0 3 GIVORS-BANS-GIVORS | GIVORS-BANS | G.BAN | GIVORS | GIVOR | 225 | 468 | 722 | 722 | 899 |  |  | 0.03 | 0.23 | 4.921 | 1 | 465
G.SYNL63WARAN | LIT 225kV N0 3 GRANDE-SYNTHE-WARANDE | GRANDE-SYNTHE | G.SYN | RANDENS | RANDE | 225 | 1308 | 1408 | 1408 | 1478 |  |  | 0.853 | 5.685 | 130.804 | 20.547 | 14198
G.CAIL63MASTA | LIT 225kV N0 3 GROS-CAILLOU-MASTAING | GROS-CAILLOU | G.CAI | MASTAING | MASTA | 225 | 975 | 1030 | 1030 | 1110 |  |  | 0.497 | 2.478 | 55.711 | 8.751 | 6105
LUMESL63MOHON | LIT 225kV N0 3 LUMES - MOHON | LUMES | LUMES | MOHON | MOHON | 225 | 328 | 554 | 554 | 694 |  |  | 0.357 | 2.325 | 53.668 | 8.43 | 5500
MEZE5L63PORCH | LIT 225kV N0 3 MEZEROLLES-PORCHEVILLE | MEZEROLLES | MEZE5 | PORCHEVILLE | PORCH | 225 | 511 | 768 | 768 | 979 |  |  | 0.366 | 2.445 | 54.95 | 8.632 | 6406
MTPELL63TAMAR | LIT 225kV N0 3 MONTPELLIER - TAMAREAU | MONTPELLIER | MTPEL | TAMAREAU | TAMAR | 225 | 1200 | 1200 | 1320 | 1389 |  |  | 1.216 | 8.161 | 248.442 | 39.025 | 20543
ORMESL63VESLE | LIT 225kV N0 3 ORMES-VESLE | ORMES | ORMES | VESLE | VESLE | 225 | 1140 | 1248 | 1248 | 1347 |  |  | 1.311 | 8.738 | 194.565 | 30.562 | 21661
P.GASL63SEINE | LIT 225kV N0 3 PLESSIS-GASSOT - SEINE | PLESSIS-GASSOT | P.GAS | SEINE | SEINE | 225 | 1796 | 1800 | 1975 | 2100 |  |  | 0.491 | 4.808 | 236.501 | 37.149 | 16391
P.SIML63VERFE | LIT 225kV N0 3 PORTET-ST-SIMON - VERFEIL | PORTET-ST-SIMON | P.SIM | VERFEIL | VERFE | 225 | 756 | 858 | 858 | 921 |  |  | 2.379 | 12.608 | 274.359 | 43.096 | 30788
REALTL63SEPTE | LIT 225kV N0 3 REALTOR - SEPTEMES | REALTOR | REALT | SEPTEMES | SEPTE | 225 | 1062 | 1160 | 1160 | 1238 |  |  | 0.382 | 2.562 | 78.464 | 12.325 | 7112
AGASSL71JONQU | LIT 400kV N0 1 AGASSES (LES) - JONQUIERES | AGASSES (LES) | AGASS | JONQUIERES | JONQU | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.206 | 2.707 | 142.744 | 22.422 | 10281
AGASSL71TAVEL | LIT 400kV N0 1 AGASSES (LES) - TAVEL | AGASSES (LES) | AGASS | TAVEL | TAVEL | 400 | 2462 | 2644 | 2644 | 2798 |  |  | 0.46 | 4.671 | 183.576 | 28.836 | 15596
ALBERL71COCHE | LIT 400kV N0 1 ALBERTVILLE - COCHE (LA) | ALBERTVILLE | ALBER | COCHE (LA) | COCHE | 400 | 2585 | 2633 | 2633 | 2715 |  |  | 0.694 | 9.818 | 203.285 | 31.932 | 22583
ALBERL71G.ILE | LIT 400kV N0 1 ALBERTVILLE - GRANDE-ILE | ALBERTVILLE | ALBER | GRANDE-ILE | G.ILE | 400 | 3099 | 3441 | 3441 | 3741 |  |  | 0.739 | 11.29 | 538.441 | 84.578 | 40744
ALBERL71M.LAN | LIT 400kV N0 1 ALBERTVILLE-MONTAGNY-LES-LANCHES | ALBERTVILLE | ALBER | MONTAGNY-LES-LANCHES | M.LAN | 400 | 2170 | 2318 | 2318 | 2498 |  |  | 1.265 | 12.616 | 443.885 | 69.725 | 37517
ARGIAL71CANTE | LIT 400kV N0 1 ARGIA (BAYONNE SUD) - CANTEGRIT | ARGIA (BAYONNE SUD) | ARGIA | CANTEGRIT | CANTE | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.608 | 29.184 | 892.872 | 140.252 | 83807
ARGOEL71CHEVA | LIT 400kV N0 1 ARGOEUVES - CHEVALET | ARGOEUVES | ARGOE | CHEVALET | CHEVA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.842 | 11.054 | 582.616 | 91.517 | 41972
ARGOEL71FRUGE | LIT 400kV N0 1 ARGOEUVES - FRUGES | ARGOEUVES | ARGOE | FRUGES | FRUGE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.307 | 17.156 | 904.261 | 142.041 | 65137
ARGOEL71LIMEU | LIT 400kV N0 1 ARGOEUVES - LIMEUX | ARGOEUVES | ARGOE | LIMEUX | LIMEU | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.492 | 8.333 | 463.586 | 72.82 | 33285
ARGOEL71MANDA | LIT 400kV N0 1 ARGOEUVES - MANDARINS | ARGOEUVES | ARGOE | MANDARINS | MANDA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.377 | 31.238 | 1648.737 | 258.983 | 118964
ARGOEL71PENL5 | LIT 400kV N0 1 ARGOEUVES - PENLY (POSTE EVACUATION) | ARGOEUVES | ARGOE | PENLY (POSTE EVACUATION) | PENL5 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.213 | 20.654 | 1146.974 | 180.166 | 80720
ARGOEL71TERRI | LIT 400kV N0 1 ARGOEUVES - TERRIER | ARGOEUVES | ARGOE | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.684 | 22.111 | 1165.88 | 183.136 | 83970
AVELIL71GAVRE | LIT 400kV N0 1 AVELIN - GAVRELLE | AVELIN | AVELI | GAVRELLE | GAVRE | 400 | 2238 | 2412 | 2412 | 2622 |  |  | 0.87 | 9.697 | 299.562 | 47.055 | 28140
AVELIL71MASTA | LIT 400kV N0 1 AVELIN - MASTAING | AVELIN | AVELI | MASTAING | MASTA | 400 | 2570 | 2718 | 2718 | 2912 |  |  | 0.91 | 10.249 | 354.191 | 55.636 | 31358
AVELIL71WEPPE | LIT 400kV N0 1 AVELIN - WEPPES | AVELIN | AVELI | WEPPES | WEPPE | 400 | 3078 | 3266 | 3266 | 3458 |  |  | 0.532 | 6.714 | 384.108 | 60.335 | 21668
AVOI5L71DISTR | LIT 400kV N0 1 AVOINE (POSTE 400 kV) - DISTRE | AVOINE (POSTE 400 KV) | AVOI5 | DISTRE | DISTR | 400 | 3196 | 3488 | 3488 | 3582 |  |  | 0.511 | 6.623 | 260.13 | 40.861 | 21655
AVOI5L71G.AVO | LIT 400kV N0 1 AVOINE (POSTE 400 kV) - GRILLE-AVOINE | AVOINE (POSTE 400 KV) | AVOI5 | GRILLE-AVOINE | G.AVO | 400 | 1950 | 2025 | 2025 | 2100 |  |  | 0.009 | 0.149 | 3.482 | 0.547 | 375
AVOI5L71LARCA | LIT 400kV N0 1 AVOINE (POSTE 400 kV) - LARCAY | AVOINE (POSTE 400 KV) | AVOI5 | LARCAY | LARCA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.009 | 13.254 | 699.704 | 109.909 | 50356
BAIXAL71GAUDI | LIT 400kV N0 1 BAIXAS - GAUDIERE (LA) | BAIXAS | BAIXA | GAUDIERE (LA) | GAUDI | 400 | 4400 | 4500 | 4500 | 4500 |  |  | 1.565 | 22.203 | 839.529 | 131.873 | 71084
BARNAL71PENL5 | LIT 400kV N0 1 BARNABOS - PENLY (POSTE EVACUATION) | BARNABOS | BARNA | PENLY (POSTE EVACUATION) | PENL5 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.707 | 12.046 | 669.312 | 105.135 | 47082
BARNAL71ROUGE | LIT 400kV N0 1 BARNABOS - ROUGEMONTIER | BARNABOS | BARNA | ROUGEMONTIER | ROUGE | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.057 | 15.342 | 608.174 | 95.532 | 50281
BARNAL71TERRI | LIT 400kV N0 1 BARNABOS - TERRIER | BARNABOS | BARNA | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.136 | 28.087 | 1484.423 | 233.173 | 106793
BARNAL71VAUPA | LIT 400kV N0 1 BARNABOS - VAUPALIERE (LA) | BARNABOS | BARNA | VAUPALIERE (LA) | VAUPA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.437 | 5.743 | 302.661 | 47.542 | 21836
BARNAL71REMIS | LIT 400kV N0 1 BARNABOS-REMISE | BARNABOS | BARNA | REMISE | REMIS | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.725 | 22.672 | 1193.517 | 187.477 | 86154
BAYETL71GREPI | LIT 400kV N0 1 BAYET - GREPILLES | BAYET | BAYET | GREPILLES | GREPI | 400 | 2130 | 2374 | 2374 | 2576 |  |  | 2.126 | 21.558 | 849.526 | 133.443 | 70752
BAYETL71MARMA | LIT 400kV N0 1 BAYET - MARMAGNE | BAYET | BAYET | MARMAGNE | MARMA | 400 | 2130 | 2300 | 2300 | 2400 |  |  | 3.707 | 37.569 | 1482.996 | 232.948 | 123205
BAYETL71RULHA | LIT 400kV N0 1 BAYET - RULHAT | BAYET | BAYET | RULHAT | RULHA | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 1.039 | 13.658 | 721.72 | 113.368 | 52395
BAYETL71GAUGL | LIT 400kV N0 1 BAYET-GAUGLIN | BAYET | BAYET | GAUGLIN | GAUGL | 400 | 2800 | 3000 | 3000 | 3100 |  |  | 3.096 | 40.844 | 2167.601 | 340.486 | 156345
BEZAUL71HOUDR | LIT 400kV N0 1 BEZAUMONT - HOUDREVILLE | BEZAUMONT | BEZAU | HOUDREVILLE | HOUDR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.038 | 13.645 | 720.143 | 113.12 | 51843
BEZAUL71MARL6 | LIT 400kV N0 1 BEZAUMONT - MARLENHEIM | BEZAUMONT | BEZAU | MARLENHEIM | MARL6 | 400 | 2070 | 2282 | 2282 | 2400 |  |  | 4.629 | 51.059 | 1989.751 | 312.549 | 166234
BEZAUL71VIGY | LIT 400kV N0 1 BEZAUMONT - VIGY | BEZAUMONT | BEZAU |  | 1VIGY | 400 | 3294 | 3622 | 3622 | 3780 |  |  | 0.886 | 11.633 | 612.618 | 96.23 | 44148
BIANCL71TRANS | LIT 400kV N0 1 BIANCON - TRANS | BIANCON | BIANC | TRANS | TRANS | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 0.936 | 9.487 | 374.496 | 58.826 | 31208
BOCTOL71M.SEI | LIT 400kV N0 1 BOCTOIS - MERY-SUR-SEINE | BOCTOIS | BOCTO | MERY-SUR-SEINE | M.SEI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.714 | 9.372 | 492.279 | 77.327 | 35548
BOCTOL71MORBR | LIT 400kV N0 1 BOCTOIS - MORBRAS | BOCTOIS | BOCTO | MORBRAS | MORBR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.565 | 20.572 | 1086.364 | 170.646 | 78180
BOISSL71CHAFF | LIT 400kV N0 1 BOISSE (LA) - CHAFFARD (LE) | BOISSE (LA) | BOISS | CHAFFARD (LE) | CHAFF | 400 | 1752 | 1998 | 1998 | 2172 |  |  | 0.724 | 7.901 | 253.983 | 39.896 | 23479
BOISSL71MIONS | LIT 400kV N0 1 BOISSE (LA) - MIONS | BOISSE (LA) | BOISS | MIONS | MIONS | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 0.617 | 6.605 | 220.834 | 34.689 | 20080
B.TOLL71GEN.P | LIT 400kV N0 1 BOIS-TOLLOT - GENISSIAT-POSTE | BOIS-TOLLOT | B.TOL | GENISSIAT-POSTE | GEN.P | 400 | 1948 | 2162 | 2162 | 2348 |  |  | 1.107 | 10.877 | 381.815 | 59.975 | 33634
BOUTRL71P.ORG | LIT 400kV N0 1 BOUTRE - PLAN-D ORGON | BOUTRE | BOUTR | PLAN-D ORGON | P.ORG | 400 | 3192 | 3489 | 3489 | 3723 |  |  | 1.659 | 21.818 | 1152.925 | 181.101 | 83165
BOUTRL71PRION | LIT 400kV N0 1 BOUTRE - PRIONNET | BOUTRE | BOUTR | PRIONNET | PRION | 400 | 3192 | 3489 | 3489 | 3723 |  |  | 0.147 | 2.356 | 108.656 | 17.068 | 8951
BRAUDL71MQIS | LIT 400kV N0 1 BRAUD - MARQUIS (LE) | BRAUD | BRAUD |  | 1MQIS | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.921 | 11.921 | 468.08 | 73.526 | 39424
BRAUDL71PREGU | LIT 400kV N0 1 BRAUD - PREGUILLAC | BRAUD | BRAUD | PREGUILLAC | PREGU | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 0.994 | 14.43 | 572.057 | 89.859 | 47291
BREUIL71MARMA | LIT 400kV N0 1 BREUIL (LE) - MARMAGNE | BREUIL (LE) | BREUI | MARMAGNE | MARMA | 400 | 1410 | 1632 | 1632 | 1806 |  |  | 9.503 | 71.427 | 2233.386 | 350.819 | 209476
BREUIL71RUEYR | LIT 400kV N0 1 BREUIL (LE) - RUEYRES | BREUIL (LE) | BREUI | RUEYRES | RUEYR | 400 | 1186 | 1644 | 1644 | 1968 |  |  | 1.964 | 21.402 | 733.04 | 115.146 | 65650
B.CARL71BIANC | LIT 400kV N0 1 BROC-CARROS (LE) - BIANCON | BROC-CARROS (LE) | B.CAR | BIANCON | BIANC | 400 | 2006 | 2192 | 2192 | 2336 |  |  | 1.665 | 15.592 | 623.881 | 97.999 | 51487
CALA5L71COR.P | LIT 400kV N0 1 CALAN - CORDEMAIS-POSTE | CALAN | CALA5 | CORDEMAIS-POSTE | COR.P | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 4.186 | 42.432 | 1673.787 | 262.918 | 139524
CALA5L71MARTY | LIT 400kV N0 1 CALAN - MARTYRE (LA) | CALAN | CALA5 | MARTYRE (LA) | MARTY | 400 | 2862 | 2920 | 2920 | 3020 |  |  | 2.953 | 29.941 | 1180.375 | 185.413 | 98335
CAPELL71LONNY | LIT 400kV N0 1 CAPELLE (LA) - LONNY | CAPELLE (LA) | CAPEL | LONNY | LONNY | 400 | 2196 | 2422 | 2422 | 2596 |  |  | 1.639 | 17.552 | 586.813 | 92.176 | 53016
CAPELL71MASTA | LIT 400kV N0 1 CAPELLE (LA) - MASTAING | CAPELLE (LA) | CAPEL | MASTAING | MASTA | 400 | 2570 | 2718 | 2718 | 2914 |  |  | 1.887 | 20.213 | 675.812 | 106.156 | 60871
CAZARL71MARSI | LIT 400kV N0 1 CAZARIL - MARSILLON | CAZARIL | CAZAR | MARSILLON | MARSI | 400 | 3316 | 3622 | 3622 | 3780 |  |  | 2.096 | 29.202 | 1485.863 | 233.399 | 101257
CAZARL71VERFE | LIT 400kV N0 1 CAZARIL - VERFEIL | CAZARIL | CAZAR | VERFEIL | VERFE | 400 | 3255 | 3600 | 3600 | 3780 |  |  | 2.421 | 32.079 | 1680.961 | 264.045 | 121353
CERGYL71MEZE5 | LIT 400kV N0 1 CERGY-MEZEROLLES | CERGY | CERGY | MEZEROLLES | MEZE5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.991 | 10.236 | 384.146 | 60.342 | 32739
CERGYL71TERRI | LIT 400kV N0 1 CERGY-TERRIER | CERGY | CERGY | TERRIER | TERRI | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 0.876 | 9.212 | 326.549 | 51.294 | 28595
CHAFFL71CPNIE | LIT 400kV N0 1 CHAFFARD (LE) - CHAMPAGNIER | CHAFFARD (LE) | CHAFF | CHAMPAGNIER | CPNIE | 400 | 2110 | 2246 | 2246 | 2382 |  |  | 3.161 | 35.012 | 1153.877 | 181.251 | 104135
CHAFFL71COULA | LIT 400kV N0 1 CHAFFARD (LE) - COULANGE | CHAFFARD (LE) | CHAFF | COULANGE | COULA | 400 | [6 empty] | 4.154 | 41.629 | 1652.193 | 259.526 | 0
CHAFFL71G.ILE | LIT 400kV N0 1 CHAFFARD (LE) - GRANDE-ILE | CHAFFARD (LE) | CHAFF | GRANDE-ILE | G.ILE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.44 | 20.469 | 1023.776 | 160.814 | 76242
CHAFFL71MIONS | LIT 400kV N0 1 CHAFFARD (LE) - MIONS | CHAFFARD (LE) | CHAFF | MIONS | MIONS | 400 | 1764 | 1876 | 1876 | 1988 |  |  | 0.543 | 4.174 | 131.144 | 20.6 | 12222
CHAFFL71P.COR | LIT 400kV N0 1 CHAFFARD (LE) - PIVOZ-CORDIER | CHAFFARD (LE) | CHAFF | PIVOZ-CORDIER | P.COR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.293 | 14.857 | 543.1 | 85.31 | 47327
CHAFFL71SSV.O | LIT 400kV N0 1 CHAFFARD (LE) - ST-VULBAS-OUEST | CHAFFARD (LE) | CHAFF | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2400 | 2400 | 2400 |  |  | 0.562 | 5.705 | 224.009 | 35.187 | 18713
CHAINL71VERGE | LIT 400kV N0 1 CHAINGY - VERGER | CHAINGY | CHAIN | VERGER | VERGE | 400 | 1332 | 1796 | 1796 | 2098 |  |  | 0.716 | 7.287 | 286.713 | 45.037 | 23926
CBRY L71M.SEI | LIT 400kV N0 1 CHAMBRY - MERY-SUR-SEINE | CHAMBRY | CBRY | MERY-SUR-SEINE | M.SEI | 400 | 1812 | 1988 | 1988 | 2124 |  |  | 4.148 | 32.015 | 988.87 | 155.331 | 93177
CBRY L71PENC5 | LIT 400kV N0 1 CHAMBRY - PENCHARD | CHAMBRY | CBRY | PENCHARD | PENC5 | 400 | 1988 | 2122 | 2122 | 2258 |  |  | 0.201 | 1.622 | 50.525 | 7.936 | 4722
CPNIEL71VAUJA | LIT 400kV N0 1 CHAMPAGNIER - VAUJANY | CHAMPAGNIER | CPNIE | VAUJANY | VAUJA | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 0.667 | 9.296 | 372.698 | 58.543 | 30750
CHAN5L71DISTR | LIT 400kV N0 1 CHANCEAUX - DISTRE | CHANCEAUX | CHAN5 | DISTRE | DISTR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.318 | 24.1 | 951.112 | 149.4 | 79080
CHAN5L71LARCA | LIT 400kV N0 1 CHANCEAUX - LARCAY | CHANCEAUX | CHAN5 | LARCAY | LARCA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.445 | 5.843 | 307.683 | 48.331 | 22164
CHAN5L71QUINT | LIT 400kV N0 1 CHANCEAUX - QUINTES (LES) | CHANCEAUX | CHAN5 | QUINTES (LES) | QUINT | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.191 | 15.651 | 826.132 | 129.768 | 59408
CHAN5L71VLERB | LIT 400kV N0 1 CHANCEAUX - VILLERBON | CHANCEAUX | CHAN5 | VILLERBON | VLERB | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.912 | 19.401 | 765.093 | 120.181 | 89280
CHARPL71ECHAL | LIT 400KV N0 1 CHARPENAY - ECHALAS | CHARPENAY | CHARP | ECHALAS | ECHAL | 400 | [6 empty] | 0.526 | 9.604 | 410.796 | 64.528 | 32890
CHARPL71GREPI | LIT 400kV N0 1 CHARPENAY - GREPILLES | CHARPENAY | CHARP | GREPILLES | GREPI | 400 | 2168 | 2308 | 2308 | 2448 |  |  | 1.777 | 17.251 | 686.547 | 107.843 | 57026
CHARPL71SSV.O | LIT 400kV N0 1 CHARPENAY - ST-VULBAS-OUEST | CHARPENAY | CHARP | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 1.696 | 17.199 | 677.682 | 106.45 | 53537
CHESNL71CIROL | LIT 400kV N0 1 CHESNOY (LE) - CIROLLIERS | CHESNOY (LE) | CHESN | CIROLLIERS | CIROL | 400 | 1022 | 1614 | 1614 | 1956 |  |  | 1.823 | 20.419 | 629.688 | 98.911 | 58648
CHESNL71M.SEI | LIT 400kV N0 1 CHESNOY (LE) - MERY-SUR-SEINE | CHESNOY (LE) | CHESN | MERY-SUR-SEINE | M.SEI | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 2.465 | 24.978 | 985.956 | 154.874 | 82163
CHESNL71MORBR | LIT 400kV N0 1 CHESNOY (LE) - MORBRAS | CHESNOY (LE) | CHESN | MORBRAS | MORBR | 400 | 2300 | 2522 | 2522 | 2696 |  |  | 1.451 | 15.877 | 518.289 | 81.413 | 47256
MORBRL71ZCHES | LIT 400kV N0 1 CHESNOY (LE) - PIQUAGE A CHESNOY | MORBRAS | MORBR |  | ZCHES | 400 | 1022 | 1614 | 1614 | 1956 |  |  | 0.025 | 0.265 | 8.869 | 1.393 | 58942
CHESNL71TABAR | LIT 400kV N0 1 CHESNOY (LE) - TABARDERIE | CHESNOY (LE) | CHESN | TABARDERIE | TABAR | 400 | 2138 | 2356 | 2356 | 2522 |  |  | 2.847 | 31.537 | 999.594 | 157.016 | 91731
CHESNL71VLECH | LIT 400kV N0 1 CHESNOY (LE) - VILLECHETIVE | CHESNOY (LE) | CHESN | VILLECHETIVE | VLECH | 400 | 1410 | 1808 | 1808 | 2116 |  |  | 2.198 | 24.353 | 771.009 | 121.11 | 71239
CHEVAL71GAVRE | LIT 400kV N0 1 CHEVALET - GAVRELLE | CHEVALET | CHEVA | GAVRELLE | GAVRE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 0.595 | 7.809 | 411.649 | 64.662 | 67140
CHEVAL71LATEN | LIT 400kV N0 1 CHEVALET - LATENA | CHEVALET | CHEVA | LATENA | LATEN | 400 | 2570 | 2718 | 2718 | 2914 |  |  | 1.977 | 20.03 | 794.838 | 124.853 | 65954
CHEVAL71WARAN | LIT 400kV N0 1 CHEVALET - WARANDE | CHEVALET | CHEVA | WARANDE | WARAN | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 3.115 | 31.604 | 1246.642 | 195.822 | 29616
CIROLL71GATI5 | LIT 400kV N0 1 CIROLLIERS - GATINAIS | CIROLLIERS | CIROL | GATINAIS | GATI5 | 400 | 2300 | 2522 | 2522 | 2696 |  |  | 1.068 | 14.027 | 740.123 | 116.258 | 19640
CIROLL71VLEJU | LIT 400kV N0 1 CIROLLIERS - VILLEJUST | CIROLLIERS | CIROL | VILLEJUST | VLEJU | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.609 | 6.8 | 208.607 | 32.768 | 53455
CLERAL71CUBNE | LIT 400kV N0 1 CLERAC - CUBNEZAIS | CLERAC | CLERA | CUBNEZAIS | CUBNE | 400 | 1850 | 2194 | 2194 | 2370 |  |  | 0.661 | 7.126 | 236.787 | 37.194 | 127980
CLERAL71PLAUD | LIT 400kV N0 1 CLERAC - PLAUD | CLERAC | CLERA | PLAUD | PLAUD | 400 | 2585 | 2633 | 2633 | 2715 |  |  | 3.972 | 44.447 | 1367.319 | 214.778 | 40341
COCHEL71P.AND | LIT 400kV N0 1 COCHE (LA) - PRAZ-ST-ANDRE | COCHE (LA) | COCHE | PRAZ-ST-ANDRE | P.AND | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.237 | 17.543 | 361.236 | 56.743 | 91000
COR.PL71LOUIS | LIT 400kV N0 1 CORDEMAIS-P - LOUISFERT (poste F) | CORDEMAIS-POSTE | COR.P | LOUISFERT | LOUIS | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.671 | 16.933 | 669.837 | 105.218 | 150881
COR.PL71GALOR | LIT 400kV N0 1 CORDEMAIS-POSTE - GALOREAUX (LES) | CORDEMAIS-POSTE | COR.P | GALOREAUX (LES) | GALOR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.738 | 26.79 | 1145.509 | 179.936 | 55189
CORNIL71GEN.P | LIT 400kV N0 1 CORNIER - GENISSIAT-POSTE | CORNIER | CORNI | GENISSIAT-POSTE | GEN.P | 400 | 2304 | 2462 | 2462 | 2654 |  |  | 0.764 | 11.675 | 549.362 | 86.294 | 68868
CORNIL71M.LAN | LIT 400kV N0 1 CORNIER - MONTAGNY-LES-LANCHES | CORNIER | CORNI | MONTAGNY-LES-LANCHES | M.LAN | 400 | 3465 | 3544 | 3544 | 3575 |  |  | 1.649 | 21.038 | 851.956 | 133.825 | 90713
COULAL71P.COR | LIT 400kV N0 1 COULANGE - PIVOZ-CORDIER | COULANGE | COULA | PIVOZ-CORDIER | P.COR | 400 | 2144 | 2284 | 2284 | 2448 |  |  | 2.725 | 27.563 | 1088.79 | 171.027 | 90708
COULAL71TAVEL | LIT 400kV N0 1 COULANGE - TAVEL | COULANGE | COULA | TAVEL | TAVEL | 400 | 2168 | 2308 | 2308 | 2448 |  |  | 2.283 | 21.794 | 902.003 | 141.686 | 45273
COULAL71TRI.P | LIT 400kV N0 1 COULANGE - TRICASTIN-POSTE (LE) | COULANGE | COULA | TRICASTIN-POSTE (LE) | TRI.P | 400 | 3465 | 3544 | 3544 | 3575 |  |  | 1.371 | 13.485 | 535.158 | 84.062 | 90713
CRENEL71M.SEI | LIT 400kV N0 1 CRENEY - MERY-SUR-SEINE | CRENEY | CRENE | MERY-SUR-SEINE | M.SEI | 400 | 2366 | 2400 | 2400 | 2600 |  |  | 1.172 | 9.065 | 281.508 | 44.219 | 83925
CRENEL71REVIG | LIT 400kV N0 1 CRENEY - REVIGNY | CRENEY | CRENE | REVIGNY | REVIG | 400 | 1684 | 1854 | 1854 | 1986 |  |  | 2.595 | 27.828 | 929.462 | 146 | 40800
CRENEL71VIELM | LIT 400kV N0 1 CRENEY - VIELMOULIN | CRENEY | CRENE | VIELMOULIN | VIELM | 400 | 2946 | 3144 | 3144 | 3344 |  |  | 5.532 | 42.281 | 1304.398 | 204.894 | 59949
CREYSL71GEN.P | LIT 400kV N0 1 CREYS - GENISSIAT-POSTE | CREYS | CREYS | GENISSIAT-POSTE | GEN.P | 400 | 2946 | 3144 | 3144 | 3344 |  |  | 1.112 | 16.141 | 687.728 | 108.028 | 21051
CREYSL71G.ILE | LIT 400kV N0 1 CREYS - GRANDE-ILE | CREYS | CREYS | GRANDE-ILE | G.ILE | 400 | 2750 | 2875 | 2875 | 3000 |  |  | 1.271 | 18.454 | 731.119 | 114.844 | 52885
CREYSL71SSV.O | LIT 400kV N0 1 CREYS - ST-VULBAS-OUEST | CREYS | CREYS | ST-VULBAS-OUEST | SSV.O | 400 | 2946 | 3144 | 3144 | 3344 |  |  | 0.445 | 6.452 | 255.518 | 40.137 | 60459
CUBNEL71DONZA | LIT 400kV N0 1 CUBNEZAIS - DONZAC | CUBNEZAIS | CUBNE | DONZAC | DONZA | 400 | 2374 | 2522 | 2522 | 2624 |  |  | 3.748 | 49.276 | 2603.404 | 408.942 | 63067
CUBNEL71SAUCA | LIT 400kV N0 1 CUBNEZAIS - SAUCATS | CUBNEZAIS | CUBNE | SAUCATS | SAUCA | 400 | 3150 | 3307 | 3307 | 3465 |  |  | 1.876 | 19.02 | 750.554 | 117.897 | 210752
DAMBRL71GATI5 | LIT 400kV N0 1 DAMBRON - GATINAIS | DAMBRON | DAMBR | GATINAIS | GATI5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.848 | 11.133 | 587.193 | 92.236 | 55100
DAMBRL71VERGE | LIT 400kV N0 1 DAMBRON - VERGER | DAMBRON | DAMBR | VERGER | VERGE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 1.664 | 16.881 | 665.889 | 104.598 | 116318
DAMBRL71YVE.O | LIT 400kV N0 1 DAMBRON-YVELINES-OUEST | DAMBRON | DAMBR | YVELINES-OUEST | YVE.O | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 3.477 | 35.298 | 1397.074 | 219.452 | 42736
DISTRL71GALOR | LIT 400kV N0 1 DISTRE - GALOREAUX (LES) | DISTRE | DISTR | GALOREAUX (LES) | GALOR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.783 | 18.026 | 718.738 | 112.899 | 46472
DISTRL71JUMEA | LIT 400kV N0 1 DISTRE - JUMEAUX (LES) | DISTRE | DISTR | JUMEAUX (LES) | JUMEA | 400 | 2494 | 2716 | 2716 | 2872 |  |  | 1.395 | 14.155 | 556.761 | 87.456 | 98933
DISTRL71PICOC | LIT 400kV N0 1 DISTRE - PICOCHERIE (LA) | DISTRE | DISTR | PICOCHERIE (LA) | PICOC | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.91 | 30.086 | 1187.676 | 186.56 | 46472
DOMLOL71LAUNA | LIT 400kV N0 1 DOMLOUP - LAUNAY | DOMLOUP | DOMLO | LAUNAY | LAUNA | 400 | 2494 | 2676 | 2676 | 2778 |  |  | 1.411 | 18.548 | 979.061 | 153.791 | 48566
DOMLOL71LOUIS | LIT 400kV N0 1 DOMLOUP - LOUISFERT (poste F) | DOMLOUP | DOMLO | LOUISFERT | LOUIS | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.469 | 14.91 | 585.913 | 92.035 | 43829
DOMLOL71OUDON | LIT 400kV N0 1 DOMLOUP - OUDON | DOMLOUP | DOMLO | OUDON | OUDON | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.921 | 11.633 | 609.598 | 95.755 | 111701
DOMLOL71P.HA5 | LIT 400kV N0 1 DOMLOUP-PLAINE HAUTE | DOMLOUP | DOMLO | PLAINE HAUTE | P.HA5 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 3.396 | 36.665 | 1256.665 | 197.396 | 70591
DONZAL71LESQU | LIT 400kV N0 1 DONZAC - LESQUIVE | DONZAC | DONZA | LESQUIVE | LESQU | 400 | 3255 | 3600 | 3600 | 3780 |  |  | 1.007 | 13.151 | 686.402 | 107.82 | 89931
ECHALL71P.COR | LIT 400KV N0 1 ECHALAS - PIVOZ-CORDIER | ECHALAS | ECHAL | PIVOZ-CORDIER | P.COR | 400 | [6 empty] | 0.268 | 4.89 | 209.17 | 32.856 | 16747
EGUZOL71MARMA | LIT 400kV N0 1 EGUZON - MARMAGNE | EGUZON | EGUZO | MARMAGNE | MARMA | 400 | 2332 | 2582 | 2582 | 2716 |  |  | 2.742 | 30.811 | 941.033 | 147.817 | 85196
EGUZOL71PLAUD | LIT 400kV N0 1 EGUZON - PLAUD | EGUZON | EGUZO | PLAUD | PLAUD | 400 | 1186 | 1644 | 1644 | 1968 |  |  | 2.64 | 29.543 | 902.936 | 141.833 | 227310
EGUZOL71RUEYR | LIT 400kV N0 1 EGUZON - RUEYRES | EGUZON | EGUZO | RUEYRES | RUEYR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 6.694 | 73.668 | 2552.101 | 400.883 | 76000
EGUZOL71VALDI | LIT 400kV N0 1 EGUZON - VALDIVIENNE | EGUZON | EGUZO | VALDIVIENNE | VALDI | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.518 | 19.985 | 1056.262 | 165.917 | 144534
EGUZOL71VERGE | LIT 400kV N0 1 EGUZON - VERGER | EGUZON | EGUZO | VERGER | VERGE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 4.171 | 45.846 | 1672.554 | 262.724 | 75954
FRASNL71GEN.P | LIT 400kV N0 1 FRASNE - GENISSIAT-POSTE | FRASNE | FRASN | GENISSIAT-POSTE | GEN.P | 400 | 2070 | 2282 | 2282 | 2400 |  |  | 3.012 | 36.863 | 1001.225 | 157.272 | 71386
FRASNL71MAMBE | LIT 400kV N0 1 FRASNE - MAMBELIN | FRASNE | FRASN | MAMBELIN | MAMBE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.068 | 22.621 | 828.622 | 130.16 | 52000
FRUGEL71MANDA | LIT 400kV N0 1 FRUGES - MANDARINS | FRUGES | FRUGE | MANDARINS | MANDA | 400 | 3195 | 3561 | 3561 | 3780 |  |  | 1.037 | 13.637 | 720.407 | 113.161 | 88758
GATI5L71GAUGL | LIT 400kV N0 1 GATINAIS - GAUGLIN | GATINAIS | GATI5 | GAUGLIN | GAUGL | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.74 | 22.883 | 1208.509 | 189.832 | 44838
GATI5L71TABAR | LIT 400kV N0 1 GATINAIS - TABARDERIE | GATINAIS | GATI5 | TABARDERIE | TABAR | 400 | 3195 | 3561 | 3561 | 3780 |  |  | 0.899 | 11.804 | 622.697 | 97.813 | 88736
GAUDIL71ISSEL | LIT 400kV N0 1 GAUDIERE (LA) - ISSEL | GAUDIERE (LA) | GAUDI | ISSEL | ISSEL | 400 | 2176 | 2400 | 2400 | 2576 |  |  | 1.775 | 17.931 | 716.084 | 112.482 | 175186
GEN.PL71VIELM | LIT 400kV N0 1 GENISSIAT-POSTE - VIELMOULIN | GENISSIAT-POSTE | GEN.P | VIELMOULIN | VIELM | 400 | 2200 | 2556 | 2556 | 2864 |  |  | 3.545 | 51.485 | 2042.332 | 320.809 | 168798
GRANZL71JUMEA | LIT 400kV N0 1 GRANZAY - JUMEAUX (LES) | GRANZAY | GRANZ | JUMEAUX (LES) | JUMEA | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 2.364 | 24.314 | 960.118 | 150.815 | 64884
GRANZL71PREGU | LIT 400kV N0 1 GRANZAY - PREGUILLAC | GRANZAY | GRANZ | PREGUILLAC | PREGU | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.35 | 19.588 | 776.608 | 121.989 | 54452
GRANZL71ROM | LIT 400kV N0 1 GRANZAY - ROM | GRANZAY | GRANZ |  | 71ROM | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.1 | 14.465 | 764.5 | 120.087 | 79955
GROSNL71SSV.O | LIT 400kV N0 1 GROSNE - ST-VULBAS-OUEST | GROSNE | GROSN | ST-VULBAS-OUEST | SSV.O | 400 | 2138 | 2356 | 2356 | 2522 |  |  | 3.567 | 39.288 | 1265.63 | 198.805 | 2840
GROSNL71VIELM | LIT 400kV N0 1 GROSNE - VIELMOULIN | GROSNE | GROSN | VIELMOULIN | VIELM | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 2.549 | 28.582 | 871.392 | 136.878 | 131583
H.PAUL71SSV.O | LIT 400kV N0 1 HENRI-PAUL - ST-VULBAS-OUEST | HENRI-PAUL | H.PAU | ST-VULBAS-OUEST | SSV.O | 400 | 3294 | 3622 | 3622 | 3780 |  |  | 2.637 | 37.126 | 1707.054 | 268.143 | 66068
H.PAUL71VIELM | LIT 400kV N0 1 HENRI-PAUL - VIELMOULIN | HENRI-PAUL | H.PAU | VIELMOULIN | VIELM | 400 | 2104 | 2300 | 2300 | 2400 |  |  | 1.349 | 17.72 | 934.591 | 146.805 | 54154
HERS5L71LATEN | LIT 400kV N0 1 HERSE(LA) - LATENA | HERSE(LA) | HERS5 | LATENA | LATEN | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.229 | 12.468 | 491.338 | 77.179 | 61754
HERS5L71VLEVA | LIT 400kV N0 1 HERSE(LA) - VILLEVAUDE | HERSE(LA) | HERS5 | VILLEVAUDE | VLEVA | 400 | 2055 | 2277 | 2277 | 2458 |  |  | 1.856 | 18.819 | 741.27 | 116.438 | 61833
HOUDRL71LOGEL | LIT 400kV N0 1 HOUDREVILLE - LOGELBACH | HOUDREVILLE | HOUDR | LOGELBACH | LOGEL | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 3.108 | 35.853 | 1229.85 | 193.184 | 109170
HOUDRL71M.SEI | LIT 400kV N0 1 HOUDREVILLE - MERY-SUR-SEINE | HOUDREVILLE | HOUDR | MERY-SUR-SEINE | M.SEI | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 4.883 | 49.515 | 1953.151 | 306.8 | 162749
HOUDRL71N.MAI | LIT 400kV N0 1 HOUDREVILLE - NEUVES-MAISONS | HOUDREVILLE | HOUDR | NEUVES-MAISONS | N.MAI | 400 | 2214 | 2450 | 2450 | 2630 |  |  | 0.333 | 3.559 | 121.262 | 19.048 | 10822
HOUDRL71VINCE | LIT 400kV N0 1 HOUDREVILLE - VINCEY | HOUDREVILLE | HOUDR | VINCEY | VINCE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 0.818 | 8.953 | 324.111 | 50.911 | 28055
ISSELL71VERFE | LIT 400kV N0 1 ISSEL - VERFEIL | ISSEL | ISSEL | VERFEIL | VERFE | 400 | 2170 | 2400 | 2400 | 2574 |  |  | 1.167 | 11.809 | 470.309 | 73.876 | 38884
JONQUL71TAVEL | LIT 400kV N0 1 JONQUIERES - TAVEL | JONQUIERES | JONQU | TAVEL | TAVEL | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.656 | 7.267 | 321.55 | 50.509 | 25040
GAUDIL71RUEYR | LIT 400kV N0 1 LA GAUDIERE - RUEYRES | GAUDIERE (LA) | GAUDI | RUEYRES | RUEYR | 400 | 3150 | 3392 | 3392 | 3590 |  |  | 5.16 | 58.181 | 1935.148 | 303.972 | 96657
GAUDIL71TAMAR | LIT 400kV N0 1 LA GAUDIERE - TAMAREAU | GAUDIERE (LA) | GAUDI | TAMAREAU | TAMAR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.036 | 29.623 | 1172.752 | 184.215 | 59184
LATENL71VLEVA | LIT 400kV N0 1 LATENA - VILLEVAUDE | LATENA | LATEN | VILLEVAUDE | VLEVA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 3.063 | 31.059 | 1223.894 | 192.249 | 82000
LAUNAL71TAUTE | LIT 400kV N0 1 LAUNAY - TAUTE | LAUNAY | LAUNA | TAUTE | TAUTE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.641 | 21.58 | 1140.537 | 179.155 | 82000
LESQUL71VERFE | LIT 400kV N0 1 LESQUIVE - VERFEIL | LESQUIVE | LESQU | VERFEIL | VERFE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.805 | 10.592 | 558.279 | 87.694 | 47228
LIMEUL71PENL5 | LIT 400kV N0 1 LIMEUX - PENLY (POSTE EVACUATION) | LIMEUX | LIMEU | PENLY (POSTE EVACUATION) | PENL5 | 400 | 2196 | 2400 | 2400 | 2596 |  |  | 0.708 | 12.09 | 670.638 | 105.344 | 30365
LOGELL71MUHLB | LIT 400kV N0 1 LOGELBACH - MUHLBACH | LOGELBACH | LOGEL | MUHLBACH | MUHLB | 400 | 2196 | 2400 | 2400 | 2596 |  |  | 0.91 | 9.249 | 361.942 | 56.854 | 10823
LONNYL71MAZUR | LIT 400kV N0 1 LONNY - MAZURES | LONNY | LONNY | MAZURES | MAZUR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.325 | 3.36 | 127.699 | 20.059 | 10770
LONNYL71SEUIL | LIT 400kV N0 1 LONNY - SEUIL | LONNY | LONNY | SEUIL | SEUIL | 400 | 3639 | 3894 | 3894 | 4149 |  |  | 0.711 | 11.811 | 651.241 | 102.297 | 75667
LONNYL71VESLE | LIT 400kV N0 1 LONNY - VESLE | LONNY | LONNY | VESLE | VESLE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.193 | 20.013 | 1106.37 | 173.788 | 118313
LONNYL71MOULA | LIT 400kV N0 1 LONNY-MOULAINE | LONNY | LONNY | MOULAINE | MOULA | 400 | 3639 | 3894 | 3894 | 4149 |  |  | 2.26 | 29.7 | 1563.756 | 245.634 | 43688
MAMBEL71SIERE | LIT 400kV N0 1 MAMBELIN - SIERENTZ | MAMBELIN | MAMBE | SIERENTZ | SIERE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.35 | 24.592 | 843.187 | 132.447 | 28604
MANDAL71WARAN | LIT 400kV N0 1 MANDARINS - WARANDE | MANDARINS | MANDA | WARANDE | WARAN | 400 | 3294 | 3622 | 3622 | 3780 |  |  | 0.572 | 7.547 | 395.767 | 62.167 | 33049
MARL6L71SCHEE | LIT 400kV N0 1 MARLENHEIM - SCHEER | MARLENHEIM | MARL6 | SCHEER | SCHEE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.663 | 8.703 | 458.869 | 72.079 | 33048
MARL6L71VIGY | LIT 400kV N0 1 MARLENHEIM-VIGY | MARLENHEIM | MARL6 |  | 1VIGY | 400 | 1838 | 2036 | 2036 | 2140 |  |  | 2.678 | 36.336 | 1887.813 | 296.537 | 86085
MARMAL71TABAR | LIT 400kV N0 1 MARMAGNE - TABARDERIE | MARMAGNE | MARMA | TABARDERIE | TABAR | 400 | 1410 | 1890 | 1890 | 2114 |  |  | 3.753 | 29.361 | 926.748 | 145.573 | 90623
MQIS L71SAUCA | LIT 400kV N0 1 MARQUIS (LE) - SAUCATS | MARQUIS (LE) | MQIS | SAUCATS | SAUCA | 400 | 1677 | 1875 | 1875 | 2100 |  |  | 1.595 | 17.587 | 572.668 | 89.955 | 6805
MENUEL71TAUTE | LIT 400kV N0 1 MENUEL - TAUTE | MENUEL | MENUE | TAUTE | TAUTE | 400 | 2662 | 2878 | 2878 | 2996 |  |  | 0.72 | 9.468 | 500.4 | 78.603 | 14300
MENUEL71TOLLE | LIT 400kV N0 1 MENUEL - TOLLEVAST | MENUEL | MENUE | TOLLEVAST | TOLLE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.428 | 4.356 | 170.175 | 26.731 | 36000
M.SEIL71VESLE | LIT 400kV N0 1 MERY-SUR-SEINE - VESLE | MERY-SUR-SEINE | M.SEI | VESLE | VESLE | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 2.504 | 26.819 | 896.669 | 140.848 | 42230
M.SEIL71VIELM | LIT 400kV N0 1 MERY-SUR-SEINE - VIELMOULIN | MERY-SUR-SEINE | M.SEI | VIELMOULIN | VIELM | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 3.149 | 45.724 | 1813.631 | 284.885 | 42210
MEZE5L71TILL5 | LIT 400kV N0 1 MEZEROLLES - TILLEUL | MEZEROLLES | MEZE5 | TILLEUL | TILL5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.123 | 21.523 | 848.851 | 133.337 | 17274
MEZE5L71YVE.O | LIT 400kV N0 1 MEZEROLLES-YVELINES-OUEST | MEZEROLLES | MEZE5 | YVELINES-OUEST | YVE.O | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.518 | 5.251 | 207.288 | 32.561 | 70228
MOLIEL71OUDON | LIT 400kV N0 1 MOLIERE - OUDON | MOLIERE | MOLIE | OUDON | OUDON | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.15 | 14.508 | 760.863 | 119.516 | 46857
MOLIEL71QUINT | LIT 400kV N0 1 MOLIERE - QUINTES (LES) | MOLIERE | MOLIE | QUINTES (LES) | QUINT | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.984 | 12.421 | 651.059 | 102.268 | 14948
MTEZ5L71RUEYR | LIT 400kV N0 1 MONTEZIC (POSTE EXTERIEUR) - RUEYRES | MONTEZIC (POSTE EXTERIEUR) | MTEZ5 | RUEYRES | RUEYR | 400 | [6 empty] | 0.163 | 2.758 | 62.039 | 9.745 | 0
MORBRL71VLEVA | LIT 400kV N0 1 MORBRAS - VILLEVAUDE | MORBRAS | MORBR | VILLEVAUDE | VLEVA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.244 | 3.966 | 237.815 | 37.356 | 15228
MOULAL71VIGY | LIT 400kV N0 1 MOULAINE - VIGY | MOULAINE | MOULA |  | 1VIGY | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.234 | 16.217 | 856.071 | 134.471 | 61622
MUHLBL71SCHEE | LIT 400kV N0 1 MUHLBACH - SCHEER | MUHLBACH | MUHLB | SCHEER | SCHEE | 400 | [6 empty] | 1.59 | 17.975 | 685.477 | 107.675 | 0
MUHLBL71VINCE | LIT 400kV N0 1 MUHLBACH - VINCEY | MUHLBACH | MUHLB | VINCEY | VINCE | 400 | 2055 | 2277 | 2277 | 2458 |  |  | 3.195 | 36.108 | 1265.376 | 198.765 | 111227
MUHLBL71SIERE | LIT 400kV N0 1 MUHLBACH-SIERENTZ | MUHLBACH | MUHLB | SIERENTZ | SIERE | 400 | 2202 | 2426 | 2426 | 2598 |  |  | 0.959 | 10.713 | 368.412 | 57.87 | 32691
NEOULL71REALT | LIT 400kV N0 1 NEOULES - REALTOR | NEOULES | NEOUL | REALTOR | REALT | 400 | 2006 | 2192 | 2192 | 2336 |  |  | 2.16 | 20.427 | 816.86 | 128.312 | 68288
NEOULL71TRANS | LIT 400kV N0 1 NEOULES - TRANS | NEOULES | NEOUL | TRANS | TRANS | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 1.357 | 13.765 | 541.759 | 85.099 | 45205
OUDONL71QUINT | LIT 400kV N0 1 OUDON - QUINTES (LES) | OUDON | OUDON | QUINTES (LES) | QUINT | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.128 | 26.892 | 1413.149 | 221.977 | 100927
OUDONL71TAUTE | LIT 400kV N0 1 OUDON - TAUTE | OUDON | OUDON | TAUTE | TAUTE | 400 | 3900 | 4050 | 4050 | 4200 |  |  | 3.26 | 42.869 | 2265.701 | 355.896 | 163000
PICOCL71VLERB | LIT 400kV N0 1 PICOCHERIE (LA) - VILLERBON | PICOCHERIE (LA) | PICOC | VILLERBON | VLERB | 400 | 2232 | 2448 | 2448 | 2666 |  |  | 0.887 | 9.007 | 353.659 | 55.553 | 29576
P.ORGL71TAVEL | LIT 400kV N0 1 PLAN-D ORGON - TAVEL | PLAN-D ORGON | P.ORG | TAVEL | TAVEL | 400 | 3192 | 3489 | 3489 | 3723 |  |  | 0.832 | 10.94 | 578.018 | 90.795 | 41812
P.GASL71PENC5 | LIT 400kV N0 1 PLESSIS-GASSOT - PENCHARD | PLESSIS-GASSOT | P.GAS | PENCHARD | PENC5 | 400 | 1988 | 2122 | 2122 | 2258 |  |  | 1.387 | 11.335 | 356.605 | 56.015 | 33225
P.GASL71SAUS5 | LIT 400kV N0 1 PLESSIS-GASSOT - SAUSSET | PLESSIS-GASSOT | P.GAS | SAUSSET | SAUS5 | 400 | 2300 | 2522 | 2522 | 2696 |  |  | 0.425 | 4.707 | 149.832 | 23.536 | 13828
P.GASL71TERRI | LIT 400kV N0 1 PLESSIS-GASSOT - TERRIER | PLESSIS-GASSOT | P.GAS | TERRIER | TERRI | 400 | 2300 | 2522 | 2522 | 2696 |  |  | 0.805 | 9.079 | 346.061 | 54.359 | 29084
P.ANDL71ZP.AN | LIT 400kV N0 1 PRAZ-ST-ANDRE - PIQUAGE A LA PRAZ-ST-ANDRE | PRAZ-ST-ANDRE | P.AND |  | ZP.AN | 400 | 1500 | 1705 | 1705 | 1800 |  |  | 0.003 | 0.058 | 2.268 | 0.356 | 170
P.ANDL71S.BIS | LIT 400kV N0 1 PRAZ-ST-ANDRE - SUPER-BISSORTE | PRAZ-ST-ANDRE | P.AND | SUPER-BISSORTE | S.BIS | 400 | 1300 | 1300 | 1300 | 1300 |  |  | 0.036 | 0.22 | 90.203 | 14.169 | 998
PRIONL71ZT.SU | LIT 400kV N0 1 PRIONNET - T.SUP / PRION - TAVEL | PRIONNET | PRION |  | ZT.SU | 400 | 3592 | 3886 | 3886 | 4094 |  |  | 0.01 | 0.187 | 7.882 | 1.238 | 635
REALTL71TAVEL | LIT 400kV N0 1 REALTOR - TAVEL | REALTOR | REALT | TAVEL | TAVEL | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 2.735 | 27.716 | 1094.04 | 171.851 | 91947
REMISL71TERRI | LIT 400kV N0 1 REMISE - TERRIER | REMISE | REMIS | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.576 | 7.565 | 397.585 | 62.452 | 28714
REVIGL71VIGY | LIT 400kV N0 1 REVIGNY - VIGY | REVIGNY | REVIG |  | 1VIGY | 400 | 2196 | 2422 | 2422 | 2596 |  |  | 3.893 | 41.123 | 1454.977 | 228.547 | 127788
ROM L71VALDI | LIT 400kV N0 1 ROM - VALDIVIENNE | ROM | ROM | VALDIVIENNE | VALDI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.969 | 12.737 | 673.177 | 105.742 | 48872
ROUGEL71TILL5 | LIT 400kV N0 1 ROUGEMONTIER - TILLEUL | ROUGEMONTIER | ROUGE | TILLEUL | TILL5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.192 | 12.086 | 476.309 | 74.818 | 41165
ROUGEL71TOURB | LIT 400kV N0 1 ROUGEMONTIER - TOURBE | ROUGEMONTIER | ROUGE | TOURBE | TOURB | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.749 | 25.373 | 1007.271 | 158.222 | 83230
SAUS5L71VLEVA | LIT 400kV N0 1 SAUSSET - VILLEVAUDE | SAUSSET | SAUS5 | VILLEVAUDE | VLEVA | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.354 | 3.946 | 123.138 | 19.342 | 11483
SEREIL71VIELM | LIT 400kV N0 1 SEREIN - VIELMOULIN | SEREIN | SEREI | VIELMOULIN | VIELM | 400 | 2138 | 2356 | 2356 | 2522 |  |  | 2.952 | 33.112 | 1011.05 | 158.815 | 95230
SEREIL71VLECH | LIT 400kV N0 1 SEREIN - VILLECHETIVE | SEREIN | SEREI | VILLECHETIVE | VLECH | 400 | 2138 | 2356 | 2356 | 2522 |  |  | 1.119 | 12.273 | 398.154 | 62.542 | 36396
SEUILL71VESLE | LIT 400kV N0 1 SEUIL - VESLE | SEUIL | SEUIL | VESLE | VESLE | 400 | 4200 | 4200 | 4200 | 4200 |  |  | 0.491 | 8.348 | 463.645 | 72.829 | 33000
SSAVOL71VIGY | LIT 400kV N0 1 ST-AVOLD - VIGY | ST-AVOLD | SSAVO |  | 1VIGY | 400 | 1245 | 1245 | 1450 | 1450 |  |  | 0.677 | 8.928 | 523.467 | 82.226 | 280
TAMARL71TAVEL | LIT 400kV N0 1 TAMAREAU - TAVEL | TAMAREAU | TAMAR | TAVEL | TAVEL | 400 | 4400 | 4500 | 4500 | 4500 |  |  | 1.995 | 28.294 | 1069.92 | 168.063 | 91000
TAUTEL71TERR6 | LIT 400kV N0 1 TAUTE - TERRETTE | TAUTE | TAUTE | TERRETTE | TERR6 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.28 | 3.682 | 194.6 | 30.568 | 13998
TAVELL71ZT.SU | LIT 400kV N0 1 TAVEL - T.SUP / PRION - TAVEL | TAVEL | TAVEL |  | ZT.SU | 400 | 3192 | 3489 | 3489 | 3723 |  |  | 2.465 | 32.883 | 1724.153 | 270.829 | 124816
TAVELL71TRI.P | LIT 400kV N0 1 TAVEL - TRICASTIN-POSTE (LE) | TAVEL | TAVEL | TRICASTIN-POSTE (LE) | TRI.P | 400 | 2212 | 2380 | 2380 | 2498 |  |  | 1.294 | 12.506 | 495.504 | 77.834 | 41959
TERR6L71TOURB | LIT 400kV N0 1 TERRETTE - TOURBE | TERRETTE | TERR6 | TOURBE | TOURB | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.466 | 21.29 | 844.628 | 132.674 | 69804
T.SUPL71ZT.SU | LIT 400kV N0 1 TORE SUPRA - T.SUP / PRION - TAVEL | TORE SUPRA | T.SUP |  | ZT.SU | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.004 | 0.048 | 1.598 | 0.251 | 144
VERGEL71VLERB | LIT 400kV N0 1 VERGER - VILLERBON | VERGER | VERGE | VILLERBON | VLERB | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.805 | 8.172 | 321.441 | 50.492 | 26844
VLAROL71ZP.AN | LIT 400kV N0 1 VILLARODIN - PIQUAGE A LA PRAZ-ST-ANDRE | VILLARODIN | VLARO |  | ZP.AN | 400 | 2585 | 2633 | 2633 | 2715 |  |  | 0.356 | 5.038 | 103.417 | 16.245 | 11475
WARANL71WEPPE | LIT 400kV N0 1 WARANDE-WEPPES | WARANDE | WARAN | WEPPES | WEPPE | 400 | 3078 | 3266 | 3266 | 3458 |  |  | 1.628 | 20.841 | 748.983 | 117.65 | 65573
ALBERL72G.ILE | LIT 400kV N0 2 ALBERTVILLE - GRANDE-ILE | ALBERTVILLE | ALBER | GRANDE-ILE | G.ILE | 400 | 3099 | 3441 | 3441 | 3741 |  |  | 0.74 | 11.298 | 538.84 | 84.641 | 40775
ARGOEL72CHEVA | LIT 400kV N0 2 ARGOEUVES - CHEVALET | ARGOEUVES | ARGOE | CHEVALET | CHEVA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.833 | 10.936 | 576.619 | 90.575 | 42230
ARGOEL72TERRI | LIT 400kV N0 2 ARGOEUVES - TERRIER | ARGOEUVES | ARGOE | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.686 | 22.134 | 1166.29 | 183.2 | 84037
ATTAQL72MANDA | LIT 400kV N0 2 ATTAQUES (LES) - MANDARINS | ATTAQUES (LES) | ATTAQ | MANDARINS | MANDA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.21 | 2.76 | 145.581 | 22.868 | 10484
ATTAQL72WARAN | LIT 400kV N0 2 ATTAQUES (LES) - WARANDE | ATTAQUES (LES) | ATTAQ | WARANDE | WARAN | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.365 | 4.799 | 253.068 | 39.752 | 18296
AVELIL72WARAN | LIT 400kV N0 2 AVELIN - WARANDE | AVELIN | AVELI | WARANDE | WARAN | 400 | 3078 | 3266 | 3266 | 3458 |  |  | 2.172 | 27.866 | 1008.657 | 158.44 | 86764
AVELIL72MASTA | LIT 400kV N0 2 AVELIN-MASTAING | AVELIN | AVELI | MASTAING | MASTA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.681 | 8.954 | 473.239 | 74.336 | 34067
AVOI5L72DISTR | LIT 400kV N0 2 AVOINE (POSTE 400 kV) - DISTRE | AVOINE (POSTE 400 KV) | AVOI5 | DISTRE | DISTR | 400 | 3196 | 3488 | 3488 | 3582 |  |  | 0.511 | 6.624 | 260.19 | 40.871 | 21629
AVOI5L72G.AVO | LIT 400kV N0 2 AVOINE (POSTE 400 kV) - GRILLE-AVOINE | AVOINE (POSTE 400 KV) | AVOI5 | GRILLE-AVOINE | G.AVO | 400 | 1604 | 1604 | 1700 | 1700 |  |  | 0.01 | 0.159 | 21.412 | 3.363 | 447
AVOI5L72LARCA | LIT 400kV N0 2 AVOINE (POSTE 400 kV) - LARCAY | AVOINE (POSTE 400 KV) | AVOI5 | LARCAY | LARCA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.008 | 13.253 | 699.618 | 109.896 | 50360
BAIXAL72GAUDI | LIT 400kV N0 2 BAIXAS - LA GAUDIERE | BAIXAS | BAIXA | GAUDIERE (LA) | GAUDI | 400 | 4400 | 4500 | 4500 | 4500 |  |  | 1.565 | 22.203 | 839.529 | 131.873 | 71263
BARNAL72ROUGE | LIT 400kV N0 2 BARNABOS - ROUGEMONTIER | BARNABOS | BARNA | ROUGEMONTIER | ROUGE | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.057 | 15.342 | 608.186 | 95.534 | 50274
BARNAL72TERRI | LIT 400kV N0 2 BARNABOS - TERRIER | BARNABOS | BARNA | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.137 | 28.109 | 1486.056 | 233.429 | 106841
BARNAL72VAUPA | LIT 400kV N0 2 BARNABOS - VAUPALIERE (LA) | BARNABOS | BARNA | VAUPALIERE (LA) | VAUPA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.438 | 5.752 | 302.767 | 47.559 | 21813
BARNAL72PENL5 | LIT 400kV N0 2 BARNABOS-PENLY (POSTE EVACUATION) | BARNABOS | BARNA | PENLY (POSTE EVACUATION) | PENL5 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.707 | 12.044 | 669.179 | 105.114 | 47082
BARNAL72REMIS | LIT 400kV N0 2 BARNABOS-REMISE | BARNABOS | BARNA | REMISE | REMIS | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.711 | 22.484 | 1186.971 | 186.449 | 86145
BAYETL72GREPI | LIT 400kV N0 2 BAYET - GREPILLES | BAYET | BAYET | GREPILLES | GREPI | 400 | 2130 | 2374 | 2374 | 2576 |  |  | 2.123 | 21.52 | 849.209 | 133.394 | 70752
BAYETL72MARMA | LIT 400kV N0 2 BAYET - MARMAGNE | BAYET | BAYET | MARMAGNE | MARMA | 400 | 2130 | 2300 | 2300 | 2400 |  |  | 3.71 | 37.594 | 1483.992 | 233.105 | 123205
BAYETL72RULHA | LIT 400kV N0 2 BAYET - RULHAT | BAYET | BAYET | RULHAT | RULHA | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 1.039 | 13.665 | 721.688 | 113.362 | 52395
BAYETL72SSELO | LIT 400kV N0 2 BAYET-ST-ELOI | BAYET | BAYET | ST-ELOI | SSELO | 400 | 2800 | 3000 | 3000 | 3100 |  |  | 1.712 | 22.502 | 1187.834 | 186.585 | 85603
B.MONL72CHAFF | LIT 400kV N0 2 BEAUMONT-MONTEUX - CHAFFARD (LE) | BEAUMONT-MONTEUX | B.MON | CHAFFARD (LE) | CHAFF | 400 | 3465 | 3544 | 3544 | 3575 |  |  | 2.261 | 22.922 | 903.91 | 141.986 | 75994
B.MONL72COULA | LIT 400kV N0 2 BEAUMONT-MONTEUX - COULANGE | BEAUMONT-MONTEUX | B.MON | COULANGE | COULA | 400 | 3465 | 3544 | 3544 | 3575 |  |  | 1.715 | 19.416 | 710.5 | 111.605 | 61247
BEZAUL72HOUDR | LIT 400kV N0 2 BEZAUMONT - HOUDREVILLE | BEZAUMONT | BEZAU | HOUDREVILLE | HOUDR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.031 | 13.545 | 714.841 | 112.287 | 51462
BEZAUL72VIGY | LIT 400kV N0 2 BEZAUMONT - VIGY | BEZAUMONT | BEZAU |  | 2VIGY | 400 | 3294 | 3622 | 3622 | 3780 |  |  | 0.887 | 11.644 | 613.012 | 96.292 | 44179
BIANCL72TRANS | LIT 400kV N0 2 BIANCON - TRANS | BIANCON | BIANC | TRANS | TRANS | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 0.936 | 9.487 | 374.496 | 58.826 | 31212
BOCTOL72M.SEI | LIT 400kV N0 2 BOCTOIS - MERY-SUR-SEINE | BOCTOIS | BOCTO | MERY-SUR-SEINE | M.SEI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.714 | 9.373 | 493.648 | 77.542 | 35572
BOCTOL72MORBR | LIT 400kV N0 2 BOCTOIS - MORBRAS | BOCTOIS | BOCTO | MORBRAS | MORBR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.606 | 21.112 | 1114.893 | 175.127 | 77983
BRAUDL72CUBNE | LIT 400kV N0 2 BRAUD - CUBNEZAIS | BRAUD | BRAUD | CUBNEZAIS | CUBNE | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 0.642 | 9.318 | 368.852 | 57.939 | 30529
BRAUDL72PREGU | LIT 400kV N0 2 BRAUD - PREGUILLAC | BRAUD | BRAUD | PREGUILLAC | PREGU | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 0.994 | 14.43 | 572.045 | 89.857 | 47366
B.CARL72BIANC | LIT 400kV N0 2 BROC-CARROS (LE)-BIANCON | BROC-CARROS (LE) | B.CAR | BIANCON | BIANC | 400 | 2006 | 2192 | 2192 | 2336 |  |  | 1.665 | 15.592 | 623.881 | 97.999 | 51487
CANTEL72SAUCA | LIT 400kV N0 2 CANTEGRIT - SAUCATS | CANTEGRIT | CANTE | SAUCATS | SAUCA | 400 | 2690 | 2822 | 2822 | 2936 |  |  | 1.943 | 25.186 | 762.776 | 119.817 | 72590
CAZARL72MARSI | LIT 400kV N0 2 CAZARIL - MARSILLON | CAZARIL | CAZAR | MARSILLON | MARSI | 400 | 3316 | 3622 | 3622 | 3780 |  |  | 2.09 | 29.12 | 1481.576 | 232.725 | 101657
CAZARL72VERFE | LIT 400kV N0 2 CAZARIL - VERFEIL | CAZARIL | CAZAR | VERFEIL | VERFE | 400 | 3255 | 3600 | 3600 | 3780 |  |  | 2.412 | 32.015 | 1681.484 | 264.127 | 121341
CERGYL72MEZE5 | LIT 400kV N0 2 CERGY-MEZEROLLES | CERGY | CERGY | MEZEROLLES | MEZE5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.99 | 10.227 | 383.808 | 60.288 | 32714
CERGYL72TERRI | LIT 400kV N0 2 CERGY-TERRIER | CERGY | CERGY | TERRIER | TERRI | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 0.879 | 9.253 | 327.768 | 51.486 | 28712
CHAFFL72CPNIE | LIT 400kV N0 2 CHAFFARD (LE) - CHAMPAGNIER | CHAFFARD (LE) | CHAFF | CHAMPAGNIER | CPNIE | 400 | 2110 | 2246 | 2246 | 2382 |  |  | 2.248 | 27.612 | 942.551 | 148.056 | 84001
CHAFFL72G.ILE | LIT 400kV N0 2 CHAFFARD (LE)-GRANDE-ILE | CHAFFARD (LE) | CHAFF | GRANDE-ILE | G.ILE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.441 | 20.472 | 1023.765 | 160.813 | 76242
CHAFFL72MIONS | LIT 400kV N0 2 CHAFFARD (LE)-MIONS | CHAFFARD (LE) | CHAFF | MIONS | MIONS | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 0.288 | 3.687 | 186.778 | 29.339 | 13304
CHAFFL72P.COR | LIT 400kV N0 2 CHAFFARD (LE)-PIVOZ-CORDIER | CHAFFARD (LE) | CHAFF | PIVOZ-CORDIER | P.COR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.293 | 14.857 | 543.1 | 85.31 | 47327
CHAFFL72SSV.O | LIT 400kV N0 2 CHAFFARD (LE)-ST-VULBAS-OUEST | CHAFFARD (LE) | CHAFF | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2400 | 2400 | 2400 |  |  | 0.562 | 5.71 | 224.058 | 35.195 | 18722
CHAINL72VERGE | LIT 400kV N0 2 CHAINGY-VERGER | CHAINGY | CHAIN | VERGER | VERGE | 400 | 1332 | 1796 | 1796 | 2098 |  |  | 0.715 | 7.275 | 286.326 | 44.976 | 24011
CPNIEL72VAUJA | LIT 400kV N0 2 CHAMPAGNIER-VAUJANY | CHAMPAGNIER | CPNIE | VAUJANY | VAUJA | 400 | 1812 | 1988 | 1988 | 2124 |  |  | 0.667 | 9.29 | 372.472 | 58.508 | 26413
CHAN5L72LARCA | LIT 400kV N0 2 CHANCEAUX - LARCAY | CHANCEAUX | CHAN5 | LARCAY | LARCA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.445 | 5.839 | 307.524 | 48.306 | 22164
CHAN5L72QUINT | LIT 400kV N0 2 CHANCEAUX-QUINTES (LES) | CHANCEAUX | CHAN5 | QUINTES (LES) | QUINT | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.191 | 15.652 | 826.159 | 129.773 | 59426
CHARPL72ECHAL | LIT 400kV N0 2 CHARPENAY-ECHALAS | CHARPENAY | CHARP | ECHALAS | ECHAL | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.533 | 9.712 | 417.219 | 65.537 | 32882
CHARPL72GREPI | LIT 400kV N0 2 CHARPENAY-GREPILLES | CHARPENAY | CHARP | GREPILLES | GREPI | 400 | 2168 | 2308 | 2308 | 2448 |  |  | 1.712 | 17.367 | 683.478 | 107.36 | 57036
CHARPL72SSV.O | LIT 400kV N0 2 CHARPENAY-ST-VULBAS-OUEST | CHARPENAY | CHARP | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 1.711 | 17.374 | 683.411 | 107.35 | 56986
CHESNL72CIROL | LIT 400kV N0 2 CHESNOY (LE)-CIROLLIERS | CHESNOY (LE) | CHESN | CIROLLIERS | CIROL | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 1.819 | 20.373 | 628.969 | 98.798 | 82187
CHESNL72M.SEI | LIT 400kV N0 2 CHESNOY (LE)-MERY-SUR-SEINE | CHESNOY (LE) | CHESN | MERY-SUR-SEINE | M.SEI | 400 | 2300 | 2400 | 2400 | 2600 |  |  | 2.468 | 25.046 | 985.823 | 154.853 | 47267
CHESNL72MORBR | LIT 400kV N0 2 CHESNOY (LE)-MORBRAS | CHESNOY (LE) | CHESN | MORBRAS | MORBR | 400 | 2814 | 3110 | 3110 | 3338 |  |  | 1.451 | 15.878 | 518.458 | 81.439 | 114626
CHESNL72TABAR | LIT 400kV N0 2 CHESNOY (LE)-TABARDERIE | CHESNOY (LE) | CHESN | TABARDERIE | TABAR | 400 | 2814 | 3110 | 3110 | 3338 |  |  | 1.854 | 26.679 | 1079.532 | 169.573 | 115433
CHEVAL72GAVRE | LIT 400kV N0 2 CHEVALET - GAVRELLE | CHEVALET | CHEVA | GAVRELLE | GAVRE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 0.598 | 7.859 | 414.346 | 65.085 | 83793
CHEVAL72LATEN | LIT 400kV N0 2 CHEVALET - LATENA | CHEVALET | CHEVA | LATENA | LATEN | 400 | 2570 | 2718 | 2718 | 2914 |  |  | 1.97 | 19.967 | 790.926 | 124.238 | 32379
CHEVAL72WARAN | LIT 400kV N0 2 CHEVALET-WARANDE | CHEVALET | CHEVA | WARANDE | WARAN | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 3.113 | 31.59 | 1246.175 | 195.749 | 53850
CIROLL72GATI5 | LIT 400kV N0 2 CIROLLIERS - GATINAIS | CIROLLIERS | CIROL | GATINAIS | GATI5 | 400 | 2300 | 2522 | 2522 | 2696 |  |  | 1.067 | 14.021 | 739.86 | 116.217 | 19807
CIROLL72VLEJU | LIT 400kV N0 2 CIROLLIERS - VILLEJUST | CIROLLIERS | CIROL | VILLEJUST | VLEJU | 400 | 1812 | 1988 | 1988 | 2124 |  |  | 0.614 | 6.865 | 210.31 | 33.035 | 21904
COR.PL72DISTR | LIT 400kV N0 2 CORDEMAIS-POSTE - DISTRE | CORDEMAIS-POSTE | COR.P | DISTRE | DISTR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 4.521 | 45.811 | 1809.192 | 284.187 | 55162
COR.PL72LOUIS | LIT 400kV N0 2 CORDEMAIS-POSTE - LOUISFERT (poste F) | CORDEMAIS-POSTE | COR.P | LOUISFERT | LOUIS | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.666 | 16.878 | 667.653 | 104.875 | 238814
COR.PL72MARTY | LIT 400kV N0 2 CORDEMAIS-POSTE - MARTYRE (LA) | CORDEMAIS-POSTE | COR.P | MARTYRE (LA) | MARTY | 400 | 3456 | 3622 | 3622 | 3780 |  |  | 7.083 | 72.149 | 2867.118 | 450.366 | 41841
COULAL72P.COR | LIT 400kV N0 2 COULANGE-PIVOZ-CORDIER | COULANGE | COULA | PIVOZ-CORDIER | P.COR | 400 | 2168 | 2308 | 2308 | 2448 |  |  | 2.706 | 27.369 | 1081.278 | 169.847 | 45546
COULAL72TRI.P | LIT 400kV N0 2 COULANGE-TRICASTIN-POSTE (LE) | COULANGE | COULA | TRICASTIN-POSTE (LE) | TRI.P | 400 | 2168 | 2308 | 2308 | 2448 |  |  | 1.404 | 13.77 | 546.793 | 85.89 | 45546
CREYSL72GEN.P | LIT 400kV N0 2 CREYS-GENISSIAT-POSTE | CREYS | CREYS | GENISSIAT-POSTE | GEN.P | 400 | 2946 | 3144 | 3144 | 3344 |  |  | 1.113 | 16.161 | 641.263 | 100.729 | 21051
CREYSL72G.ILE | LIT 400kV N0 2 CREYS-GRANDE-ILE | CREYS | CREYS | GRANDE-ILE | G.ILE | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 1.271 | 18.452 | 731.048 | 114.833 | 52924
CREYSL72SSV.O | LIT 400kV N0 2 CREYS-ST-VULBAS-OUEST | CREYS | CREYS | ST-VULBAS-OUEST | SSV.O | 400 | 3150 | 3307 | 3307 | 3465 |  |  | 0.445 | 6.448 | 255.363 | 40.112 | 187570
CUBNEL72DONZA | LIT 400kV N0 2 CUBNEZAIS-DONZAC | CUBNEZAIS | CUBNE | DONZAC | DONZA | 400 | 2258 | 2400 | 2400 | 2600 |  |  | 3.716 | 48.855 | 2581.127 | 405.442 | 12719
CUBNEL72MQIS | LIT 400kV N0 2 CUBNEZAIS-MARQUIS (LE) | CUBNEZAIS | CUBNE |  | 2MQIS | 400 | 2374 | 2522 | 2522 | 2624 |  |  | 0.371 | 3.923 | 150.871 | 23.699 | 63062
CUBNEL72SAUCA | LIT 400kV N0 2 CUBNEZAIS-SAUCATS | CUBNEZAIS | CUBNE | SAUCATS | SAUCA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.887 | 19.144 | 755.08 | 118.608 | 42309
DAMBRL72GATI5 | LIT 400kV N0 2 DAMBRON - GATINAIS | DAMBRON | DAMBR | GATINAIS | GATI5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.848 | 11.136 | 587.339 | 92.259 | 55106
DAMBRL72VLEJU | LIT 400kV N0 2 DAMBRON - VILLEJUST | DAMBRON | DAMBR | VILLEJUST | VLEJU | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.138 | 21.707 | 852.697 | 133.941 | 59000
DAMBRL72VERGE | LIT 400kV N0 2 DAMBRON-VERGER | DAMBRON | DAMBR | VERGER | VERGE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 1.664 | 16.882 | 665.379 | 104.518 | 73751
DISTRL72JUMEA | LIT 400kV N0 2 DISTRE - JUMEAUX (LES) | DISTRE | DISTR | JUMEAUX (LES) | JUMEA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.394 | 14.142 | 557.955 | 87.643 | 70591
DOMLOL72LAUNA | LIT 400kV N0 2 DOMLOUP - LAUNAY | DOMLOUP | DOMLO | LAUNAY | LAUNA | 400 | 2494 | 2676 | 2676 | 2778 |  |  | 1.412 | 18.552 | 979.261 | 153.822 | 48525
DOMLOL72LOUIS | LIT 400kV N0 2 DOMLOUP - LOUISFERT (poste F) | DOMLOUP | DOMLO | LOUISFERT | LOUIS | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.469 | 14.91 | 585.913 | 92.035 | 43888
DOMLOL72OUDON | LIT 400kV N0 2 DOMLOUP - OUDON | DOMLOUP | DOMLO | OUDON | OUDON | 400 | 3255 | 3600 | 3600 | 3780 |  |  | 0.95 | 12.008 | 629.248 | 98.842 | 49674
DONZAL72VERFE | LIT 400kV N0 2 DONZAC-VERFEIL | DONZAC | DONZA | VERFEIL | VERFE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.797 | 23.746 | 1245.845 | 195.697 | 16746
ECHALL72P.COR | LIT 400kV N0 2 ECHALAS-PIVOZ-CORDIER | ECHALAS | ECHAL | PIVOZ-CORDIER | P.COR | 400 | 2170 | 2300 | 2300 | 2400 |  |  | 0.268 | 4.901 | 208.756 | 32.791 | 88692
EGUZOL72VALDI | LIT 400kV N0 2 EGUZON-VALDIVIENNE | EGUZON | EGUZO | VALDIVIENNE | VALDI | 400 | 1600 | 1772 | 1772 | 1904 |  |  | 1.517 | 19.973 | 1055.649 | 165.821 | 22401
GATI5L72GAUGL | LIT 400kV N0 2 GATINAIS - GAUGLIN | GATINAIS | GATI5 | GAUGLIN | GAUGL | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.752 | 22.99 | 1212.315 | 190.43 | 44839
GATI5L72TABAR | LIT 400kV N0 2 GATINAIS - TABARDERIE | GATINAIS | GATI5 | TABARDERIE | TABAR | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.899 | 11.804 | 622.71 | 97.815 | 59272
GAUGLL72SSELO | LIT 400kV N0 2 GAUGLIN-ST-ELOI | GAUGLIN | GAUGL | ST-ELOI | SSELO | 400 | 2200 | 2556 | 2556 | 2800 |  |  | 1.417 | 18.639 | 984.276 | 154.61 | 70839
GEN.PL72VIELM | LIT 400kV N0 2 GENISSIAT-POSTE-VIELMOULIN | GENISSIAT-POSTE | GEN.P | VIELMOULIN | VIELM | 400 | 1236 | 1236 | 1236 | 1236 |  |  | 3.537 | 51.373 | 2037.901 | 320.113 | 2342
GRANZL72JUMEA | LIT 400kV N0 2 GRANZAY - JUMEAUX (LES) | GRANZAY | GRANZ | JUMEAUX (LES) | JUMEA | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 2.364 | 24.317 | 959.56 | 150.727 | 64873
GRANZL72PREGU | LIT 400kV N0 2 GRANZAY - PREGUILLAC | GRANZAY | GRANZ | PREGUILLAC | PREGU | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.349 | 19.588 | 776.596 | 121.987 | 103445
GRANZL72VALDI | LIT 400kV N0 2 GRANZAY - VALDIVIENNE | GRANZAY | GRANZ | VALDIVIENNE | VALDI | 400 | 2238 | 2382 | 2382 | 2526 |  |  | 2.069 | 27.226 | 1437.471 | 225.797 | 114700
HAVR5L72ROUGE | LIT 400kV N0 2 HAVRE (LE) (POSTE) - ROUGEMONTIER | HAVRE (LE) (POSTE) | HAVR5 | ROUGEMONTIER | ROUGE | 400 | 2104 | 2300 | 2300 | 2400 |  |  | 1.685 | 17.036 | 631.958 | 99.268 | 54154
HOUDRL72M.SEI | LIT 400kV N0 2 HOUDREVILLE-MERY-SUR-SEINE | HOUDREVILLE | HOUDR | MERY-SUR-SEINE | M.SEI | 400 | 2170 | 2400 | 2400 | 2574 |  |  | 4.883 | 49.523 | 1953.442 | 306.846 | 38918
ISSELL72VERFE | LIT 400kV N0 2 ISSEL - VERFEIL | ISSEL | ISSEL | VERFEIL | VERFE | 400 | 2462 | 2644 | 2644 | 2798 |  |  | 1.169 | 11.866 | 466.586 | 73.291 | 25681
GAUDIL72ISSEL | LIT 400kV N0 2 LA GAUDIERE - ISSEL | GAUDIERE (LA) | GAUDI | ISSEL | ISSEL | 400 | 3150 | 3392 | 3392 | 3590 |  |  | 1.776 | 18.018 | 709.282 | 111.414 | 97047
GAUDIL72TAMAR | LIT 400kV N0 2 LA GAUDIERE - TAMAREAU | GAUDIERE (LA) | GAUDI | TAMAREAU | TAMAR | 400 | 3195 | 3561 | 3561 | 3780 |  |  | 2.036 | 28.774 | 1204.252 | 189.164 | 70830
LAUNAL72TAUTE | LIT 400kV N0 2 LAUNAY-TAUTE | LAUNAY | LAUNA | TAUTE | TAUTE | 400 | 3255 | 3600 | 3600 | 3780 |  |  | 1.641 | 21.579 | 1140.509 | 179.151 | 40283
LONNYL72MASTA | LIT 400kV N0 2 LONNY-MASTAING | LONNY | LONNY | MASTAING | MASTA | 400 | 2196 | 2400 | 2400 | 2596 |  |  | 2.374 | 31.112 | 1641.942 | 257.916 | 10831
LONNYL72MAZUR | LIT 400kV N0 2 LONNY-MAZURES | LONNY | LONNY | MAZURES | MAZUR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.325 | 3.339 | 128.632 | 20.205 | 10831
LONNYL72MOULA | LIT 400kV N0 2 LONNY-MOULAINE | LONNY | LONNY | MOULAINE | MOULA | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.259 | 29.692 | 1563.395 | 245.577 | 118211
MARMAL72TABAR | LIT 400kV N0 2 MARMAGNE-TABARDERIE | MARMAGNE | MARMA | TABARDERIE | TABAR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 2.791 | 30.898 | 980.641 | 154.039 | 36000
MENUEL72TAUTE | LIT 400kV N0 2 MENUEL-TAUTE | MENUEL | MENUE | TAUTE | TAUTE | 400 | 2662 | 2878 | 2878 | 2996 |  |  | 0.729 | 9.584 | 506.516 | 79.563 | 14300
MENUEL72TOLLE | LIT 400kV N0 2 MENUEL-TOLLEVAST | MENUEL | MENUE | TOLLEVAST | TOLLE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.429 | 4.347 | 171.743 | 26.977 | 36000
M.SEIL72VIELM | LIT 400kV N0 2 MERY-SUR-SEINE-VIELMOULIN | MERY-SUR-SEINE | M.SEI | VIELMOULIN | VIELM | 400 | 2070 | 2282 | 2282 | 2400 |  |  | 3.147 | 45.696 | 1812.517 | 284.709 | 80781
MEZE5L72TILL5 | LIT 400kV N0 2 MEZEROLLES - TILLEUL | MEZEROLLES | MEZE5 | TILLEUL | TILL5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 2.106 | 21.35 | 842.184 | 132.29 | 58720
MEZE5L72VLEJU | LIT 400kV N0 2 MEZEROLLES - VILLEJUST | MEZEROLLES | MEZE5 | VILLEJUST | VLEJU | 400 | 3780 | 3780 | 3780 | 4095 |  |  | 1.802 | 18.299 | 719.223 | 112.975 | 54911
MORBRL72VLEVA | LIT 400kV N0 2 MORBRAS - VILLEVAUDE | MORBRAS | MORBR | VILLEVAUDE | VLEVA | 400 | [6 empty] | 0.233 | 3.897 | 216.329 | 33.981 | 15218
MOULAL72VIGY | LIT 400kV N0 2 MOULAINE-VIGY | MOULAINE | MOULA |  | 2VIGY | 400 | 2070 | 2272 | 2272 | 2410 |  |  | 1.233 | 16.21 | 855.725 | 134.417 | 52745
MUHLBL72SIERE | LIT 400kV N0 2 MUHLBACH-SIERENTZ | MUHLBACH | MUHLB | SIERENTZ | SIERE | 400 | 2202 | 2425 | 2426 | 2598 |  |  | 1.3 | 10.7 | 284.569 | 44.7 | 300
NEOULL72TRANS | LIT 400kV N0 2 NEOULES - TRANS | NEOULES | NEOUL | TRANS | TRANS | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 1.357 | 13.765 | 541.759 | 85.099 | 45110
NEOULL72REALT | LIT 400kV N0 2 NEOULES-REALTOR | NEOULES | NEOUL | REALTOR | REALT | 400 | 2006 | 2192 | 2192 | 2336 |  |  | 2.16 | 20.427 | 816.86 | 128.312 | 68288
OUDONL72TAUTE | LIT 400kV N0 2 OUDON - TAUTE | OUDON | OUDON | TAUTE | TAUTE | 400 | 3900 | 4050 | 4050 | 4200 |  |  | 3.26 | 42.869 | 2265.7 | 355.895 | 163000
P.GASL72TERRI | LIT 400kV N0 2 PLESSIS-GASSOT - TERRIER | PLESSIS-GASSOT | P.GAS | TERRIER | TERRI | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.802 | 8.904 | 351.462 | 55.208 | 29093
P.ANDL72ZP.AN | LIT 400kV N0 2 PRAZ-ST-ANDRE - PIQUAGE A LA PRAZ-ST-ANDRE | PRAZ-ST-ANDRE | P.AND |  | ZP.AN | 400 | 2585 | 2633 | 2633 | 2715 |  |  | 0.003 | 0.049 | 1.932 | 0.303 | 138
REALTL72TAVEL | LIT 400kV N0 2 REALTOR - TAVEL | REALTOR | REALT | TAVEL | TAVEL | 400 | 2128 | 2326 | 2326 | 2482 |  |  | 2.731 | 27.719 | 1093.632 | 171.787 | 91947
REMISL72TERRI | LIT 400kV N0 2 REMISE - TERRIER | REMISE | REMIS | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.576 | 7.568 | 398.809 | 62.645 | 28730
ROUGEL72TOURB | LIT 400kV N0 2 ROUGEMONTIER - TOURBE | ROUGEMONTIER | ROUGE | TOURBE | TOURB | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.735 | 25.184 | 999.985 | 157.077 | 83032
ROUGEL72TILL5 | LIT 400kV N0 2 ROUGEMONTIER-TILLEUL | ROUGEMONTIER | ROUGE | TILLEUL | TILL5 | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 1.192 | 12.086 | 476.309 | 74.818 | 41201
TAMARL72TAVEL | LIT 400kV N0 2 TAMAREAU - TAVEL | TAMAREAU | TAMAR | TAVEL | TAVEL | 400 | 4400 | 4500 | 4500 | 4500 |  |  | 2.009 | 28.503 | 1077.827 | 169.305 | 91000
TAUTEL72TERR6 | LIT 400kV N0 2 TAUTE-TERRETTE | TAUTE | TAUTE | TERRETTE | TERR6 | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.28 | 3.682 | 194.6 | 30.568 | 13998
TAVELL72TRI.P | LIT 400kV N0 2 TAVEL - TRICASTIN-POSTE (LE) | TAVEL | TAVEL | TRICASTIN-POSTE (LE) | TRI.P | 400 | 2212 | 2380 | 2380 | 2498 |  |  | 1.294 | 12.506 | 495.504 | 77.834 | 41878
TERR6L72TOURB | LIT 400kV N0 2 TERRETTE - TOURBE | TERRETTE | TERR6 | TOURBE | TOURB | 400 | 3416 | 3622 | 3622 | 3780 |  |  | 1.469 | 21.342 | 845.986 | 132.887 | 69974
VERGEL72VLERB | LIT 400kV N0 2 VERGER - VILLERBON | VERGER | VERGE | VILLERBON | VLERB | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.806 | 8.182 | 321.677 | 50.529 | 26822
ALBERL73G.ILE | LIT 400kV N0 3 ALBERTVILLE - GRANDE-ILE | ALBERTVILLE | ALBER | GRANDE-ILE | G.ILE | 400 | 1926 | 2112 | 2112 | 2178 |  |  | 1.665 | 18.949 | 405.896 | 63.758 | 44337
ARGOEL73TERRI | LIT 400kV N0 3 ARGOEUVES - TERRIER | ARGOEUVES | ARGOE | TERRIER | TERRI | 400 | 1514 | 1794 | 1794 | 2100 |  |  | 2.634 | 25.809 | 951.036 | 149.388 | 81806
BRAUDL73CUBNE | LIT 400kV N0 3 BRAUD - CUBNEZAIS | BRAUD | BRAUD | CUBNEZAIS | CUBNE | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 0.673 | 9.771 | 386.795 | 60.758 | 32014
CANTEL73SAUCA | LIT 400kV N0 3 CANTEGRIT - SAUCATS | CANTEGRIT | CANTE | SAUCATS | SAUCA | 400 | 2690 | 2822 | 2822 | 2936 |  |  | 1.942 | 25.172 | 762.352 | 119.75 | 71813
CHAFFL73SSV.O | LIT 400kV N0 3 CHAFFARD (LE) - ST-VULBAS-OUEST | CHAFFARD (LE) | CHAFF | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2400 | 2400 | 2400 |  |  | 0.569 | 5.784 | 226.912 | 35.643 | 18945
CHESNL73TABAR | LIT 400kV N0 3 CHESNOY (LE) - TABARDERIE | CHESNOY (LE) | CHESN | TABARDERIE | TABAR | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 1.838 | 26.463 | 1064.985 | 167.287 | 29657
CIROLL73VLEJU | LIT 400kV N0 3 CIROLLIERS-VILLEJUST | CIROLLIERS | CIROL | VILLEJUST | VLEJU | 400 | 1850 | 2194 | 2194 | 2370 |  |  | 0.928 | 7.271 | 243.524 | 38.253 | 21490
COULAL73TRI.P | LIT 400kV N0 3 COULANGE - TRICASTIN-POSTE (LE) | COULANGE | COULA | TRICASTIN-POSTE (LE) | TRI.P | 400 | 2600 | 2700 | 2700 | 2800 |  |  | 1.404 | 13.77 | 546.793 | 85.89 | 30772
GEN.PL73VIELM | LIT 400kV N0 3 GENISSIAT-POSTE - VIELMOULIN | GENISSIAT-POSTE | GEN.P | VIELMOULIN | VIELM | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 7.59 | 58.345 | 1806.382 | 283.746 | 79944
HAVR5L73ROUGE | LIT 400kV N0 3 HAVRE (LE) (POSTE) - ROUGEMONTIER | HAVRE (LE) (POSTE) | HAVR5 | ROUGEMONTIER | ROUGE | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 1.684 | 17.027 | 631.624 | 99.215 | 40976
LONNYL73MASTA | LIT 400kV N0 3 LONNY-MASTAING | LONNY | LONNY | MASTAING | MASTA | 400 | 2366 | 2596 | 2596 | 2778 |  |  | 2.361 | 31.053 | 1641.215 | 257.801 | 80779
MENUEL73TAUTE | LIT 400kV N0 3 MENUEL-TAUTE | MENUEL | MENUE | TAUTE | TAUTE | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.72 | 9.468 | 500.4 | 78.603 | 36170
P.GASL73TERRI | LIT 400kV N0 3 PLESSIS-GASSOT - TERRIER | PLESSIS-GASSOT | P.GAS | TERRIER | TERRI | 400 | 3465 | 3622 | 3622 | 3780 |  |  | 0.551 | 7.223 | 379.203 | 59.565 | 27362
TAVELL73TRI.P | LIT 400kV N0 3 TAVEL - TRICASTIN-POSTE (LE) | TAVEL | TAVEL | TRICASTIN-POSTE (LE) | TRI.P | 400 | 2334 | 2470 | 2470 | 2596 |  |  | 1.686 | 15.385 | 649.824 | 102.074 | 51028
BRAUDL74CUBNE | LIT 400kV N0 4 BRAUD - CUBNEZAIS | BRAUD | BRAUD | CUBNEZAIS | CUBNE | 400 | 3072 | 3414 | 3414 | 3598 |  |  | 0.674 | 9.78 | 387.163 | 60.815 | 32045
CHAFFL74SSV.O | LIT 400kV N0 4 CHAFFARD (LE) - ST-VULBAS-OUEST | CHAFFARD (LE) | CHAFF | ST-VULBAS-OUEST | SSV.O | 400 | 2300 | 2450 | 2450 | 2600 |  |  | 0.569 | 5.778 | 226.734 | 35.615 | 20979
MENUEL74TAUTE | LIT 400kV N0 4 MENUEL-TAUTE | MENUEL | MENUE | TAUTE | TAUTE | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.72 | 9.468 | 500.4 | 78.603 | 70763
P.GASL74TERRI | LIT 400kV N0 4 PLESSIS-GASSOT - TERRIER | PLESSIS-GASSOT | P.GAS | TERRIER | TERRI | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.552 | 7.225 | 379.35 | 59.588 | 27372
P.GASL74VLEVA | LIT 400kV N0 4 PLESSIS-GASSOT - VILLEVAUDE | PLESSIS-GASSOT | P.GAS | VILLEVAUDE | VLEVA | 400 | 2200 | 2300 | 2300 | 2400 |  |  | 0.785 | 8.731 | 272.521 | 42.808 | 25401
TAVELL74TRI.P | LIT 400kV N0 4 TAVEL - TRICASTIN-POSTE (LE) | TAVEL | TAVEL | TRICASTIN-POSTE (LE) | TRI.P | 400 | 3900 | 4050 | 4050 | 4200 |  |  | 0.589 | 10.034 | 555.189 | 87.209 | 39048
TAVELL75TRI.P | LIT 400kV N0 5 TAVEL - TRICASTIN-POSTE (LE) | TAVEL | TAVEL | TRICASTIN-POSTE (LE) | TRI.P | 400 | 3900 | 4050 | 4050 | 4200 |  |  | 0.589 | 10.025 | 554.671 | 87.128 | 39045

## Tielines
|  | Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
| Circuit name | Full name | Short name | Full name | Short name | Voltage level (kV) | Summer | Interseason 1 | Interseason 2 | Winter | DLRmin (A) | DLRmax (A) | Resistance R (Ω) | Reactance X (Ω) | Capacity (nF) | Half-Susceptance Hd/2 (μS) | Length (m)
.AUBAL61MOULA | LIT 225kV N0 1 AUBANGE - MOULAINE | AUBANGE | .AUBA | MOULAINE | MOULA | 225 | 1161 | 1230 | 1230 | 1300 | - | - | 0.791 | 6.325 | 135.316 | 21.255 | 15204
.AUBAL61M.MA5 | LIT 225kV N0 1 AUBANGE - MT-SAINT-MARTIN | AUBANGE | .AUBA | MT-SAINT-MARTIN | M.MA5 | 225 | 1161 | 1230 | 1230 | 1300 | - | - | 0.235 | 1.879 | 40.21 | 6.316 | 4518
.CAMPL61ZMENT | LIT 225KV N0 1 CAMPOROSSO - MENTO / .CAM | CAMPOROSSO | .CAMP | MENTON/TRINITE VICTOR | ZMENT | 225 | 950 | 1093 | 1093 | 1165 | - | - | 0.73 | 4.42 | 98.146 | 15.417 | 10893
.EICHL61VOGEL | LIT 225kV N0 1 EICHSTETTEN - VOGELGRUN | EICHSTETTEN | .EICH | VOGELGRUN | VOGEL | 225 | 1100 | 1100 | 1100 | 1283 | - | - | 1.073 | 5.952 | 32.37 | 5.085 | 18417
.ENSDL61SSAVO | LIT 225kV N0 1 ENSDORF - ST-AVOLD | ENSDORF | .ENSD | ST-AVOLD | SSAVO | 225 | 740 | 740 | 740 | 740 | - | - | 1.671 | 7.682 | 317.579 | 49.885 | 20319
.MONCL61CHOO5 | LIT 225kV N0 1 MONCEAU - CHOOZ | MONCEAU | .MONC | CHOOZ | CHOO5 | 225 | 1057 | 1120 | 1120 | 1184 | - | - | 3.085 | 22.481 | 346.519 | 54.431 | 57994
.ACHEL71LONNY | LIT 400kV N0 1 ACHENE - LONNY | ACHENE | .ACHE | LONNY | LONNY | 400 | 2000 | 2120 | 2120 | 2240 | - | - | 1.57 | 19.76 | 776.676 | 122 | 64164
.AVELL71MASTA | LIT 400kV N0 1 AVELGEM - MASTAING | AVELGEM | .AVEL | MASTAING | MASTA | 400 | 2000 | 2120 | 2120 | 2240 | - | - | 1.885 | 22.003 | 983.36 | 154.466 | 76148
.EICHL71MUHLB | LIT 400kV N0 1 EICHSTETTEN - MUHLBACH | EICHSTETTEN | .EICH | MUHLBACH | MUHLB | 400 | 2559 | 2559 | 2559 | 2850 | - | - | 0.763 | 8.205 | 223.499 | 35.107 | 31792
.ENSDL71VIGY | LIT 400kV N0 1 ENSDORF - VIGY | ENSDORF | .ENSD | VIGY | VIGY | 400 | 2720 | 2720 | 2720 | 2720 | - | - | 0.736 | 10.275 | 569.171 | 89.405 | 40209
.RONDL71ALBER | LIT 400KV N0 1 RONDISSONE - ALBERTVILLE | RONDISSONE | .ROND | ALBERTVILLE | ALBER | 400 | 1890 | 1890 | 1890 | 2370 | - | - | 3.028 | 53.581 | 3014.25 | 473.477 | 173270
.VENAL71VLARO | LIT 400KV N0 1 VENAUS - VILLARODIN | VENAUS | .VENA | VILLARODIN | VLARO | 400 | 2585 | 2633 | 2633 | 2715 | - | - | 0.96 | 11.59 | 276.683 | 43.461 | 29308
.AVELL72AVELI | LIT 400kV N0 2 AVELGEM - AVELIN | AVELGEM | .AVEL | AVELIN | AVELI | 400 | 2322 | 2461 | 2461 | 2600 | - | - | 1.068 | 13.566 | 493.227 | 77.476 | 19619
.ENSDL72VIGY | LIT 400kV N0 2 ENSDORF - VIGY | ENSDORF | .ENSD | VIGY | VIGY | 400 | 2720 | 2720 | 2720 | 2720 | - | - | 0.735 | 10.272 | 568.965 | 89.373 | 40195
.RONDL72ALBER | LIT 400KV N0 2 RONDISSONE - ALBERTVILLE | RONDISSONE | .ROND | ALBERTVILLE | ALBER | 400 | 1890 | 1890 | 1890 | 2370 | - | - | 3.029 | 53.551 | 3014.331 | 473.49 | 173233

## Transformers
Location |  | Voltage Level U (kV) |  | Maximum Current Imax (A) primary |  | Electrical Parameters | [7 empty] | Phase Shifting Properties
Full Name | Short Name | Primary | Secondary | Summer Period | Winter Period | Rd1 à Prise moy / One-phase resistance at medium tap | Xd1 à Prise moy / One-phase reactance at medium tap | Rd2 à Prise moy / Two-phase resistance at medium tap | Xd2 à Prise moy / Two-phase reactance at medium tap | Rd3 à Prise moy / Three-phase resistance at medium tap | Xd3 à Prise moy / Three-phase reactance at medium tap | U1r sur Prise moy / Primary voltage | U2r sur Prise moy / Secondary voltage | Taps used during FB Qualification | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%)
TRANSF. 400/225kV 762 ALBERTVILLE | ALBER-Y762 | 400 | 225 | 1659 | 1803 | 0.24 | 43.1 | 0.28 | -7.9 | 2.42 | 120.2 | 388 | 240
TRANSF. 400/225kV 763 ALBERTVILLE | ALBER-Y763 | 400 | 225 | 1575 | 1803 | 0.11 | 45.9 | 0.35 | -10 | 5.47 | 129.1 | 388 | 240
TRANSF. 400/225kV 761 ARGIA (BAYONNE SUD) | ARGIA-Y761 | 400 | 225 | 1659 | 1803 | 0.17 | 42.4 | 0.31 | -6.8 | 4.89 | 124.7 | 388 | 240
TRANSF. 400/225kV 761 ARGOEUVES | ARGOE-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 45.2 | 0.21 | -9.1 | 2.58 | 122.3 | 388 | 240
TRANSF. 400/225kV 763 ARGOEUVES | ARGOE-Y763 | 400 | 225 | 1659 | 1803 | 0.31 | 46.2 | 0.18 | -9.8 | 2.56 | 123.2 | 388 | 240
TRANSF. 400/225kV 761 ATTAQUES (LES) | ATTAQ-Y761 | 400 | 225 | 847 | 921 | 0.01 | 74.3 | 0.95 | -4.5 | 6.88 | 297.8 | 380 | 235
TRANSF. 400/225kV 762 ATTAQUES (LES) | ATTAQ-Y762 | 400 | 225 | 847 | 921 | 0.37 | 68.1 | 0.76 | -10.9 | 4.9 | 209.9 | 380 | 235
TRANSF. 400/225kV 761 AVELIN | AVELI-Y761 | 400 | 225 | 1659 | 1803 | 0.29 | 45.7 | 0.21 | -9.4 | 2.61 | 122.1 | 388 | 240
TRANSF. 400/225kV 762 AVELIN | AVELI-Y762 | 400 | 225 | 1659 | 1803 | 0.28 | 45.2 | 0.21 | -9.2 | 2.62 | 122.4 | 388 | 240
TRANSF. 400/225kV 763 AVELIN | AVELI-Y763 | 400 | 225 | 1659 | 1803 | 0.28 | 45.4 | 0.21 | -9.4 | 2.6 | 120.1 | 388 | 240
TRANSF. 400/225kV 761 AVOINE (POSTE 400 KV) | AVOI5-Y761 | 400 | 225 | 840 | 913 | 0.51 | 69.4 | 0.65 | -12.4 | 5.01 | 205.8 | 380 | 235
TRANSF. 400/225kV 761 BROC-CARROS (LE) | B.CAR-Y761 | 400 | 225 | 1659 | 1803 | 0.1 | 42.3 | 0.36 | -6.5 | 4.94 | 123.5 | 388 | 240
TRANSF. 400/225kV 762 BROC-CARROS (LE) | B.CAR-Y762 | 400 | 225 | 1659 | 1803 | 0.26 | 45.5 | 0.22 | -9.3 | 2.53 | 121.1 | 388 | 240
TRANSF. 400/225kV 761 BEAUMONT-MONTEUX | B.MON-Y761 | 400 | 225 | 1659 | 1803 | 0.23 | 45.3 | 0.21 | -9.4 | 2.39 | 121.5 | 388 | 240
TRANSF. 400/225kV 762 BEAUMONT-MONTEUX | B.MON-Y762 | 400 | 225 | 1659 | 1803 | 0.25 | 45.4 | 0.18 | -9.6 | 2.46 | 120.6 | 388 | 240
TRANSF. 400/225kV 761 BAIXAS | BAIXA-Y761 | 400 | 225 | 829 | 901 | 2.2643 | 74.1 | 1.08 | -9.1 | 8.88 | 206.5 | 405 | 240
TRANSF. 400/225kV 762 BAIXAS | BAIXA-Y762 | 400 | 225 | 829 | 901 | 2.3134 | 73.8 | 1.06 | -9.3 | 8.78 | 206.3 | 405 | 240
TRANSF. 400/225kV 763 BAIXAS | BAIXA-Y763 | 400 | 225 | 830 | 902 | -0.029 | 73.15 | 1.07 | -8.78 | 8.77 | 205.7 | 405 | 240
TRANSF. 400/225kV 761 BAYET | BAYET-Y761 | 400 | 225 | 847 | 921 | 0.62 | 70 | 0.54 | -13.8 | 5.42 | 209.2 | 380 | 235
TRANSF. 400/225kV 762 BAYET | BAYET-Y762 | 400 | 225 | 775 | 910 | 0.71 | 70.5 | 0.51 | -13 | 5.32 | 212.5 | 380 | 235
TRANSF. 400/225kV 763 BAYET | BAYET-Y763 | 400 | 225 | 795 | 921 | 0.68 | 70.6 | 0.54 | -13 | 5.35 | 215.4 | 380 | 235
TRANSF. 400/225kV 761 BEZAUMONT | BEZAU-Y761 | 400 | 225 | 847 | 921 | 0.16 | 70.6 | 1.13 | -7.4 | 6.95 | 307.4 | 380 | 235
TRANSF. 400/225kV 762 BEZAUMONT | BEZAU-Y762 | 400 | 225 | 847 | 921 | 0.15 | 71.3 | 0.85 | -8.1 | 6.69 | 307.6 | 380 | 235
TRANSF. 400/225kV 761 BIANCON | BIANC-Y761 | 400 | 225 | 1620 | 1803 | 0.24 | 43.1 | 0.28 | -7.9 | 2.42 | 120.2 | 388 | 240
TRANSF. 400/225kV 762 BIANCON | BIANC-Y762 | 400 | 225 | 1620 | 1803 | 0.24 | 43.1 | 0.28 | -7.9 | 2.42 | 120.2 | 388 | 240
TRANSF. 400/225kV 761 BOISSE (LA) | BOISS-Y761 | 400 | 225 | 1659 | 1803 | 0.07 | 42.4 | 0.39 | -6.5 | 4.89 | 124.5 | 388 | 240
TRANSF. 400/225kV 762 BOISSE (LA) | BOISS-Y762 | 400 | 225 | 1659 | 1803 | 0.1 | 39.8 | 0.51 | -4 | 4.74 | 121.2 | 388 | 240
TRANSF. 400/225kV 761 BOUTRE | BOUTR-Y761 | 400 | 225 | 1659 | 1803 | 0.08 | 42.3 | 0.4 | -6.4 | 5 | 124.7 | 388 | 240
TRANSF. 400/225kV 762 BOUTRE | BOUTR-Y762 | 400 | 225 | 1620 | 1800 | 0.09 | 42.6 | 0.38 | -6.9 | 4.87 | 120.3 | 388 | 240
TRANSF. 400/225kV 761 BRAUD | BRAUD-Y761 | 400 | 225 | 884 | 961 | 0.05 | 70.3 | 0.96 | -7 | 8.14 | 305 | 380 | 235
TRANSF. 400/225kV 762 BREUIL (LE) | BREUI-Y762 | 400 | 225 | 847 | 921 | 0.4 | 68.6 | 0.75 | -11.3 | 4.98 | 206.3 | 380 | 235
TRANSF. 400/225kV 761 CALAN | CALA5-Y761 | 400 | 225 | 1540 | 1803 | 0.082 | 45.95 | 0.373 | -9.98 | 5.504 | 129.82 | 388 | 240
TRANSF. 400/225kV 761 CANTEGRIT | CANTE-Y761 | 400 | 225 | 1659 | 1803 | 0.09 | 42.5 | 0.39 | -6.6 | 4.93 | 121.8 | 388 | 240
TRANSF. 400/225kV 762 CANTEGRIT | CANTE-Y762 | 400 | 225 | 1659 | 1803 | 0.06 | 42.7 | 0.42 | -6.6 | 4.92 | 123.4 | 388 | 240
TRANSF. 400/225kV 761 CAPELLE (LA) | CAPEL-Y761 | 400 | 225 | 1445 | 1803 | 0.087 | 45.77 | 0.374 | -9.99 | 5.575 | 128.7 | 388 | 240
TRANSF. 400/225kV 761 CAZARIL | CAZAR-Y761 | 400 | 225 | 847 | 921 | 0.43 | 69.9 | 0.72 | -12.1 | 4.95 | 207.1 | 380 | 235
TRANSF. 400/225kV 762 CAZARIL | CAZAR-Y762 | 400 | 225 | 810 | 847 | 0.55 | 68.9 | 0.47 | -12.6 | 4.86 | 204.1 | 380 | 235
TRANSF. 400/225kV 761-(769) CERGY | CERGY-Y761 | 400 | 225 | 814 | 850 | 0.59 | 68.7 | 0.41 | -12.7 | 4.93 | 204.2 | 380 | 235
TRANSF. 400/225kV 763 CERGY | CERGY-Y763 | 400 | 225 | 1655 | 1800 | 0.24 | 45.4 | 0.24 | -8.9 | 2.6 | 120.8 | 388 | 240
TRANSF. 400/225kV 764 CERGY | CERGY-Y764 | 400 | 225 | 1655 | 1800 | 0.27 | 45.9 | 0.22 | -9.3 | 2.61 | 123.1 | 388 | 240
TRANSF. 400/225kV 765 CERGY | CERGY-Y765 | 400 | 225 | 1600 | 1800 | 0.26 | 45.2 | 0.17 | -9.2 | 2.63 | 122.3 | 388 | 240
TRANSF. 400/225kV 769 CERGY | CERGY-Y769 | 400 | 225 | 850 | 925 | 0.57 | 72.8 | 0.58 | -12.8 | 5.23 | 224 | 380 | 235
TRANSF. 400/225kV 761 CHAINGY | CHAIN-Y761 | 400 | 225 | 1655 | 1800 | 0.23 | 45.2 | 0.24 | -9.7 | 2.48 | 121.7 | 388 | 240
TRANSF. 400/225kV 762 CHAINGY | CHAIN-Y762 | 400 | 225 | 1655 | 1800 | 0.25 | 44.7 | 0.21 | -9.3 | 2.54 | 122.8 | 388 | 240
TRANSF. 400/225kV 761 CHARPENAY | CHARP-Y761 | 400 | 225 | 847 | 921 | 0.57 | 71.2 | 0.56 | -13.3 | 6.1 | 214.8 | 380 | 235
TRANSF. 400/225kV 762 CHARPENAY | CHARP-Y762 | 400 | 225 | 847 | 921 | 0.05 | 70.9 | 0.91 | -7.5 | 6.72 | 308 | 380 | 235
TRANSF. 400/225kV 761 CHESNOY (LE) | CHESN-Y761 | 400 | 225 | 1659 | 1803 | 0.14 | 42.3 | 0.33 | -6.2 | 4.81 | 123.9 | 388 | 240
TRANSF. 400/225kV 762 CHESNOY (LE) | CHESN-Y762 | 400 | 225 | 847 | 921 | 0.08 | 42.4 | 0.38 | -6.7 | 4.79 | 136.5 | 388 | 240
TRANSF. 400/225kV 763 CHESNOY (LE) | CHESN-Y763 | 400 | 225 | 1659 | 1803 | 0.126 | 45.66 | 0.328 | -9.82 | 5.486 | 129.21 | 388 | 240
TRANSF. 400/225kV 761 CIROLLIERS | CIROL-Y761 | 400 | 225 | 1659 | 1803 | 0.32 | 45.7 | 0.17 | -9.4 | 2.55 | 122.5 | 388 | 240
TRANSF. 400/225kV 762 CIROLLIERS | CIROL-Y762 | 400 | 225 | 1659 | 1803 | 0.28 | 45.8 | 0.21 | -9.3 | 2.58 | 121.9 | 388 | 240
TRANSF. 400/225kV 763 CIROLLIERS | CIROL-Y763 | 400 | 225 | 1659 | 1803 | 0.25 | 45.8 | 0.19 | -9.5 | 2.39 | 121.2 | 388 | 240
TRANSF. 400/225kV 761 CORDEMAIS-POSTE | COR.P-Y761 | 400 | 225 | 1659 | 1803 | 0.29 | 45.8 | 0.19 | -9.8 | 2.55 | 121.2 | 388 | 240
TRANSF. 400/225kV 763 CORDEMAIS-POSTE | COR.P-Y763 | 400 | 225 | 1659 | 1803 | 0.07 | 42.4 | 0.4 | -6.5 | 4.85 | 124.9 | 388 | 240
TRANSF. 400/225kV 765 CORDEMAIS-POSTE | COR.P-Y765 | 400 | 225 | 847 | 921 | 0.7 | 70.4 | 0.48 | -13.7 | 5.49 | 213 | 380 | 235
TRANSF. 400/225kV 769 CORDEMAIS-POSTE | COR.P-Y769 | 400 | 225 | 847 | 921 | 0.43 | 63 | 0.56 | -8.5 | 5.53 | 280.5 | 380 | 235
TRANSF. 400/225kV 761 CORNIER | CORNI-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 45.5 | 0.19 | -9.2 | 2.49 | 120.2 | 388 | 240
TRANSF. 400/225kV 762 CORNIER | CORNI-Y762 | 400 | 225 | 1630 | 1803 | 0.27 | 45.7 | 0.2 | -9.1 | 2.49 | 119.6 | 388 | 240
TRANSF. 400/225kV 761 CHAMPAGNIER | CPNIE-Y761 | 400 | 225 | 1659 | 1803 | 0.11 | 42.4 | 0.35 | -6.7 | 4.98 | 121.7 | 388 | 240
TRANSF. 400/225kV 762 CHAMPAGNIER | CPNIE-Y762 | 400 | 225 | 1659 | 1803 | 0.09 | 42.6 | 0.39 | -6.6 | 4.91 | 121.5 | 388 | 240
TRANSF. 400/225kV 765 CRENEY | CRENE-Y765 | 400 | 225 | 845 | 884 | 0.35 | 45.4 | 0.58 | -10.6 | 3.2 | 125.1 | 380 | 225
TRANSF. 400/225kV 766 CRENEY | CRENE-Y766 | 400 | 225 | 847 | 885 | 0.37 | 36.5 | 0.61 | -4.1 | 4.27 | 95.6 | 380 | 225
TRANSF. 400/225kV 768 CRENEY | CRENE-Y768 | 400 | 225 | 1659 | 1803 | 0.11 | 42.4 | 0.35 | -6.5 | 4.91 | 124.8 | 388 | 240
TRANSF. 400/225kV 761 CUBNEZAIS | CUBNE-Y761 | 400 | 225 | 1655 | 1800 | 0.29 | 44.8 | 0.19 | -9.2 | 2.61 | 122.4 | 388 | 240
TRANSF. 400/225kV 762 CUBNEZAIS | CUBNE-Y762 | 400 | 225 | 1655 | 1800 | 0.05 | 42.4 | 0.4 | -6.5 | 4.72 | 123.6 | 388 | 240
TRANSF. 400/225kV 761 DAMBRON | DAMBR-Y761 | 400 | 225 | 1655 | 1800 | 0.09 | 42.4 | 0.38 | -6.5 | 5.01 | 124.8 | 388 | 240
TRANSF. 400/225kV 760 DISTRE | DISTR-Y760 | 400 | 225 | 1659 | 1803 | 0.05 | 42.5 | 0.42 | -6.6 | 4.89 | 122 | 388 | 240
TRANSF. 400/225kV 762 DISTRE | DISTR-Y762 | 400 | 225 | 840 | 913 | 0.57 | 72.8 | 0.58 | -12.8 | 4.88 | 221.3 | 380 | 235
TRANSF. 400/225kV 765 DISTRE | DISTR-Y765 | 400 | 225 | 849 | 923 | 0.15 | 74.8 | 0.9 | -11.7 | 6.9 | 298.9 | 380 | 235
TRANSF. 400/225kV 766 DISTRE | DISTR-Y766 | 400 | 225 | 1659 | 1803 | 0.03 | 42.4 | 0.44 | -6.5 | 4.88 | 125 | 388 | 240
TRANSF. 400/225kV 764 DOMLOUP | DOMLO-Y764 | 400 | 225 | 1659 | 1803 | 0.25 | 43.7 | 0.23 | -8.4 | 2.59 | 118.5 | 388 | 240
TRANSF. 400/225kV 765 DOMLOUP | DOMLO-Y765 | 400 | 225 | 1659 | 1803 | 0.09 | 42.6 | 0.4 | -6.8 | 5.02 | 121.4 | 388 | 240
TRANSF. 400/225kV 762 DONZAC | DONZA-Y762 | 400 | 225 | 1659 | 1803 | 0.13 | 42.2 | 0.34 | -6.4 | 5.03 | 124.8 | 388 | 240
TRANSF. 400/225kV 761 ECHALAS | ECHAL-Y761 | 400 | 225 | 1659 | 1803 | 0.27 | 45.7 | 0.21 | -9.5 | 2.64 | 125.5 | 388 | 240
TRANSF. 400/225kV 762 ECHALAS | ECHAL-Y762 | 400 | 225 | 1659 | 1803 | 0.07 | 42.5 | 0.41 | -6.5 | 4.98 | 124.3 | 388 | 240
TRANSF. 400/225kV 761 EGUZON | EGUZO-Y761 | 400 | 225 | 1659 | 1803 | 0.27 | 44.8 | 0.21 | -9.1 | 2.62 | 123.4 | 388 | 240
TRANSF. 400/225kV 762 EGUZON | EGUZO-Y762 | 400 | 225 | 847 | 921 | 0.25 | 68.3 | 0.77 | -5.7 | 1.93 | 302 | 380 | 235
TRANSF. 400/225kV 761 FEUILLANE | FEUIL-Y761 | 400 | 225 | 1659 | 1803 | 0.111 | 39.8 | 0.23 | -4.27 | 4.45 | 132.2 | 388 | 240
TRANSF. 400/225kV 761 FRASNE | FRASN-Y761 | 400 | 225 | 830 | 902 | 0.004 | 74.25 | 1.049 | -9.3 | 8.797 | 208.09 | 405 | 240
TRANSF. 400/225kV 761 GRANDE-ILE | G.ILE-Y761 | 400 | 225 | 847 | 921 | 0.02 | 70.6 | 1.01 | -8.1 | 5.08 | 302 | 380 | 235
TRANSF. 400/225kV 762 GRANDE-ILE | G.ILE-Y762 | 400 | 225 | 815 | 921 | 0.45 | 71.2 | 0.66 | -7.9 | 1.34 | 290.9 | 380 | 235
TRANSF. 400/225kV 761 GALOREAUX (LES) | GALOR-Y761 | 400 | 225 | 1659 | 1803 | 0.119 | 39.64 | 0.225 | -4.53 | 4.406 | 130.6 | 388 | 240
TRANSF. 400/225kV 761 GAUDIERE (LA) | GAUDI-Y761 | 400 | 225 | 847 | 921 | 0.86 | 74.5 | 0.34 | -17.7 | 6 | 216 | 380 | 235
TRANSF. 400/225kV 762 GAUDIERE (LA) | GAUDI-Y762 | 400 | 225 | 1660 | 1805 | 0.07 | 42.7 | 0.4 | -6.8 | 4.96 | 124.8 | 388 | 240
TRANSF. 400/225kV 761 GAVRELLE | GAVRE-Y761 | 400 | 225 | 1659 | 1803 | 0.12 | 42.2 | 0.34 | -6.4 | 4.87 | 124.2 | 388 | 240
TRANSF. 400/225kV 761 GENISSIAT-POSTE | GEN.P-Y761 | 400 | 225 | 1659 | 1803 | 0.03 | 42.3 | 0.45 | -6.6 | 4.83 | 124.7 | 388 | 240
TRANSF. 400/225kV 762 GENISSIAT-POSTE | GEN.P-Y762 | 400 | 225 | 1540 | 1803 | 0.33 | 42.3 | 0.11 | -6.2 | 4.82 | 122.2 | 388 | 240
TRANSF. 400/225kV 761 GRANZAY | GRANZ-Y761 | 400 | 225 | 1659 | 1803 | 0.19 | 44.9 | 0.27 | -9.3 | 2.51 | 124.4 | 388 | 240
TRANSF. 400/225kV 762 GRANZAY | GRANZ-Y762 | 400 | 225 | 1659 | 1803 | 0.24 | 45 | 0.25 | -9.2 | 2.64 | 125 | 388 | 240
TRANSF. 400/225kV 763 GRANZAY | GRANZ-Y763 | 400 | 225 | 1659 | 1803 | 0.31 | 45.6 | 0.21 | -9.3 | 2.7 | 119.2 | 388 | 240
TRANSF. 400/225kV 761 GROSNE | GROSN-Y761 | 400 | 225 | 1659 | 1803 | 0.23 | 45 | 0.22 | -8.9 | 2.43 | 120.4 | 388 | 240
TRANSF. 400/225kV 762 GROSNE | GROSN-Y762 | 400 | 225 | 1659 | 1803 | 0.1 | 45.4 | 0.35 | -9.5 | 5.11 | 129.5 | 388 | 240
TRANSF. 400/225kV 762 HENRI-PAUL | H.PAU-Y762 | 400 | 225 | 1660 | 1805 | 0.087 | 45.55 | 0.365 | -9.7 | 5.572 | 129.4 | 388 | 240
TRANSF. 400/225kV 762 HAVRE (LE) (POSTE) | HAVR5-Y762 | 400 | 225 | 1659 | 1803 | 0.11 | 42.5 | 0.35 | -6.7 | 4.9 | 121.7 | 388 | 240
TRANSF. 400/225kV 763 HAVRE (LE) (POSTE) | HAVR5-Y763 | 400 | 225 | 1659 | 1803 | 0.06 | 42.3 | 0.4 | -6.6 | 4.79 | 123.8 | 388 | 240
TRANSF. 400/225kV 761 JONQUIERES | JONQU-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 45.4 | 0.18 | -9.2 | 2.45 | 120.6 | 388 | 240
TRANSF. 400/225kV 762 JONQUIERES | JONQU-Y762 | 400 | 225 | 1659 | 1803 | 0.29 | 45.6 | 0.19 | -9.2 | 2.53 | 120.3 | 388 | 240
TRANSF. 400/225kV 761 JUMEAUX (LES) | JUMEA-Y761 | 400 | 225 | 847 | 921 | 0.1 | 70.1 | 0.9 | -6.8 | 6.8 | 290.8 | 380 | 235
TRANSF. 400/225kV 762 JUMEAUX (LES) | JUMEA-Y762 | 400 | 225 | 847 | 921 | 0.44 | 69.3 | 0.71 | -11.8 | 5.03 | 210.8 | 380 | 235
TRANSF. 400/225kV 761 LATENA | LATEN-Y761 | 400 | 225 | 1659 | 1803 | 0.26 | 45.5 | 0.22 | -9.6 | 2.58 | 120.4 | 388 | 240
TRANSF. 400/225kV 762 LATENA | LATEN-Y762 | 400 | 225 | 1659 | 1803 | 0.27 | 45 | 0.21 | -9.2 | 2.56 | 119.5 | 388 | 240
TRANSF. 400/225kV 763 LATENA | LATEN-Y763 | 400 | 225 | 1659 | 1803 | 0.27 | 45.4 | 0.19 | -9.1 | 2.49 | 119.3 | 388 | 240
TRANSF. 400/225kV 763 LAUNAY | LAUNA-Y763 | 400 | 225 | 845 | 918 | 0.68 | 70.4 | 0.54 | -13.2 | 5.45 | 210.9 | 380 | 235
TRANSF. 400/225kV 761 LESQUIVE | LESQU-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 45.4 | 0.2 | -9.3 | 2.58 | 121.2 | 388 | 240
TRANSF. 400/225kV 762 LESQUIVE | LESQU-Y762 | 400 | 225 | 1659 | 1803 | 0.36 | 46.1 | 0.12 | -9.4 | 2.61 | 119.8 | 388 | 240
TRANSF. 400/225kV 761 LIMEUX | LIMEU-Y761 | 400 | 225 | 1659 | 1803 | 0.12 | 39.5 | 0.223 | -4.38 | 4.479 | 131 | 388 | 240
TRANSF. 400/225kV 766 LOGELBACH | LOGEL-Y766 | 400 | 225 | 840 | 913 | 0.64 | 69.9 | 0.53 | -13.2 | 5.38 | 212.5 | 380 | 235
TRANSF. 400/225kV 767 LOGELBACH | LOGEL-Y767 | 400 | 225 | 840 | 913 | 0.57 | 70.3 | 0.62 | -13.2 | 5.11 | 210 | 380 | 235
TRANSF. 400/225kV 761 MAMBELIN | MAMBE-Y761 | 400 | 225 | 840 | 913 | 0.22 | 70 | 0.74 | -7.8 | 7.17 | 300.6 | 380 | 235
TRANSF. 400/225kV 762 MAMBELIN | MAMBE-Y762 | 400 | 225 | 840 | 913 | 0.19 | 70.9 | 0.78 | -8 | 7.02 | 302.8 | 380 | 235
TRANSF. 400/225kV 763 MAMBELIN | MAMBE-Y763 | 400 | 225 | 840 | 913 | 0.17 | 68.7 | 0.8 | -6.1 | 7.02 | 302.5 | 380 | 235
TRANSF. 400/225kV 761 MANDARINS | MANDA-Y761 | 400 | 225 | 847 | 921 | 0.35 | 73 | 0.63 | -7.5 | 6.91 | 310.3 | 380 | 235
TRANSF. 400/225kV 763 MANDARINS | MANDA-Y763 | 400 | 225 | 847 | 921 | 0.35 | 72 | 0.64 | -6.9 | 6.89 | 310 | 380 | 235
TRANSF. 400/225kV 761 MARLENHEIM | MARL6-Y761 | 400 | 225 | 1659 | 1803 | 0.06 | 42.4 | 0.42 | -6.5 | 5 | 124.6 | 388 | 240
TRANSF. 400/225kV 762 MARLENHEIM | MARL6-Y762 | 400 | 225 | 1659 | 1803 | 0.08 | 44.2 | 0.38 | -8.4 | 4.95 | 122.2 | 388 | 240
TRANSF. 400/225kV 763 MARLENHEIM | MARL6-Y763 | 400 | 225 | 1659 | 1803 | 0.22 | 44.9 | 0.24 | -8.6 | 2.49 | 118.7 | 388 | 240
TRANSF. 400/225kV 761 MARMAGNE | MARMA-Y761 | 400 | 225 | 1659 | 1803 | 0.11 | 45.87 | 0.34 | -10.06 | 5.59 | 129.39 | 388 | 240
TRANSF. 400/225kV 761 MARSILLON | MARSI-Y761 | 400 | 225 | 1660 | 1805 | 1.0633 | 45.62 | 0.73849 | -9.69 | 0.02035 | 129.13 | 388 | 240
TRANSF. 400/225kV 761 MARTYRE (LA) | MARTY-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 46 | 0.21 | -9.4 | 2.61 | 120.6 | 388 | 240
TRANSF. 400/225kV 762 MARTYRE (LA) | MARTY-Y762 | 400 | 225 | 1659 | 1803 | 0.27 | 45.8 | 0.2 | -9.2 | 2.59 | 121.3 | 388 | 240
TRANSF. 400/225kV 761 MASTAING | MASTA-Y761 | 400 | 225 | 1659 | 1803 | 0.29 | 45.6 | 0.2 | -9.5 | 2.56 | 122.3 | 388 | 240
TRANSF. 400/225kV 762 MASTAING | MASTA-Y762 | 400 | 225 | 1659 | 1803 | 0.15 | 42.5 | 0.32 | -6.6 | 5.03 | 124.8 | 388 | 240
TRANSF. 400/225kV 761 MAZURES | MAZUR-Y761 | 400 | 225 | 847 | 921 | 0.36 | 69.3 | 0.64 | -7 | 7.06 | 296.3 | 380 | 235
TRANSF. 400/225kV 762 MAZURES | MAZUR-Y762 | 400 | 225 | 847 | 921 | 0.73 | 67.6 | 0.44 | -10.3 | 5.31 | 211.3 | 380 | 235
TRANSF. 400/225kV 763 MAZURES | MAZUR-Y763 | 400 | 225 | 1650 | 1803 | 0.11 | 42.2 | 0.35 | -6.6 | 4.94 | 121.5 | 388 | 240
TRANSF. 400/225kV 761 MEZEROLLES | MEZE5-Y761 | 400 | 225 | 1659 | 1803 | 0.27 | 45.4 | 0.22 | -9.3 | 2.7 | 122.8 | 388 | 240
TRANSF. 400/225kV 762 MEZEROLLES | MEZE5-Y762 | 400 | 225 | 847 | 921 | 0.54 | 69.6 | 0.64 | -13.2 | 4.89 | 207 | 380 | 235
TRANSF. 400/225kV 763 MEZEROLLES | MEZE5-Y763 | 400 | 225 | 1659 | 1803 | 0.14 | 42.4 | 0.31 | -6.3 | 2.59 | 124 | 388 | 240
TRANSF. 400/225kV 764 MEZEROLLES | MEZE5-Y764 | 400 | 225 | 1659 | 1803 | 0.28 | 45.5 | 0.21 | -9.6 | 2.64 | 123.3 | 388 | 240
TRANSF. 400/225kV 761 MIONS | MIONS-Y761 | 400 | 225 | 1659 | 1803 | 0.14 | 42.4 | 0.33 | -6.6 | 5.01 | 125.1 | 388 | 240
TRANSF. 400/225kV 762 MIONS | MIONS-Y762 | 400 | 225 | 1659 | 1803 | 0.14 | 42 | 0.31 | -6.4 | 4.85 | 120.1 | 388 | 240
TRANSF. 400/225kV 763 MIONS | MIONS-Y763 | 400 | 225 | 1630 | 1803 | 0.22 | 45 | 0.23 | -8.8 | 2.48 | 119.5 | 388 | 240
TRANSF. 400/225kV 761 MORBRAS | MORBR-Y761 | 400 | 225 | 1659 | 1803 | 0.25 | 45.4 | 0.22 | -9.1 | 2.46 | 121.5 | 388 | 240
TRANSF. 400/225kV 762 MORBRAS | MORBR-Y762 | 400 | 225 | 1659 | 1803 | 0.27 | 45.5 | 0.22 | -9.5 | 2.58 | 122.1 | 388 | 240
TRANSF. 400/225kV 763 MORBRAS | MORBR-Y763 | 400 | 225 | 1659 | 1803 | 0.28 | 45.2 | 0.21 | -8.9 | 2.65 | 123.5 | 388 | 240
TRANSF. 400/225kV 764 MORBRAS | MORBR-Y764 | 400 | 225 | 1659 | 1803 | 0.31 | 45.4 | 0.18 | -9.4 | 2.66 | 120 | 388 | 240
TRANSF. 400/225kV 761 MOULAINE | MOULA-Y761 | 400 | 225 | 1659 | 1803 | 0.44 | 36.1 | 0.75 | -9.54 | 0.021 | 128.58 | 388 | 240
TRANSF. 400/225kV 762 MOULAINE | MOULA-Y762 | 400 | 225 | 1659 | 1803 | 0.11 | 42.6 | 0.37 | -6.7 | 4.92 | 119.9 | 388 | 240
TRANSF. 400/225kV 761 MARQUIS (LE) | MQIS -Y761 | 400 | 225 | 845 | 884 | 0.55 | 73.1 | 0.65 | -20.8 | 5.39 | 212.8 | 380 | 225
TRANSF. 400/225kV 762 MARQUIS (LE) | MQIS -Y762 | 400 | 225 | 1659 | 1803 | 0.53 | 73 | 0.68 | -19.8 | 5.46 | 212 | 380 | 225
TRANSF. 400/225kV 763 MARQUIS (LE) | MQIS -Y763 | 400 | 225 | 845 | 884 | 0.41 | 62.7 | 0.75 | -12.3 | 5.64 | 191.3 | 380 | 225
TRANSF. 400/225kV 764 MARQUIS (LE) | MQIS -Y764 | 400 | 225 | 1659 | 1803 | 0.099 | 40.11 | 0.245 | -4.58 | 4.407 | 131.9 | 388 | 240
TRANSF. 400/225kV 761 NEOULES | NEOUL-Y761 | 400 | 225 | 1659 | 1803 | 0.13 | 42 | 0.34 | -6.2 | 4.91 | 122.5 | 388 | 240
TRANSF. 400/225kV 762 NEOULES | NEOUL-Y762 | 400 | 225 | 1659 | 1803 | 0.28 | 45.1 | 0.21 | -9 | 2.59 | 120.3 | 388 | 240
TRANSF. 400/225kV 761 OUDON | OUDON-Y761 | 400 | 225 | 1659 | 1803 | 0.14 | 44.8 | 0.31 | -5.89 | 3.57 | 89 | 405 | 240
TRANSF. 400/225kV 761 PRAZ-ST-ANDRE | P.AND-Y761 | 400 | 225 | 847 | 921 | 0.11 | 67.9 | 0.87 | -6 | 7.09 | 296.8 | 380 | 235
TRANSF. 400/225kV 761 PLESSIS-GASSOT | P.GAS-Y761 | 400 | 225 | 1655 | 1800 | 0.32 | 45.9 | 0.16 | -9.6 | 2.56 | 122.1 | 388 | 240
TRANSF. 400/225kV 762 PLESSIS-GASSOT | P.GAS-Y762 | 400 | 225 | 1655 | 1800 | 0.08 | 42.3 | 0.39 | -6.4 | 5 | 124.6 | 388 | 240
TRANSF. 400/225kV 763 PLESSIS-GASSOT | P.GAS-Y763 | 400 | 225 | 1655 | 1800 | 0.29 | 45.2 | 0.22 | -9.6 | 2.68 | 122.8 | 388 | 240
TRANSF. 400/225kV 764 PLESSIS-GASSOT | P.GAS-Y764 | 400 | 225 | 1600 | 1800 | 0.28 | 44.6 | 0.22 | -8.9 | 2.56 | 118 | 388 | 240
TRANSF. 400/225kV 765 PLESSIS-GASSOT | P.GAS-Y765 | 400 | 225 | 1655 | 1800 | 0.28 | 45.1 | 0.19 | -9.1 | 2.51 | 121.1 | 388 | 240
TRANSF. 400/225kV 762 PLAINE HAUTE | P.HA5-Y762 | 400 | 225 | 1659 | 1803 | 0.098 | 39.63 | 0.244 | -4.53 | 4.385 | 130.37 | 388 | 240
TRANSF. 400/225kV 763 PLAINE HAUTE | P.HA5-Y763 | 400 | 225 | 1659 | 1803 | 0.31 | 45.8 | 0.18 | -9.4 | 2.57 | 121.3 | 388 | 240
TRANSF. 400/225kV 761 PLAN-D ORGON | P.ORG-Y761 | 400 | 225 | 847 | 921 | 0.25 | 76.4 | 0.74 | -8.3 | 7.14 | 302.8 | 380 | 235
TRANSF. 400/225kV 761 PONTEAU | PONTE-Y761 | 400 | 225 | 1659 | 1803 | 0.068 | -11.7 | 0.38 | -9.7 | 5.48 | -8.25 | 388 | 240
TRANSF. 400/225kV 761 QUINTES (LES) | QUINT-Y761 | 400 | 225 | 1659 | 1803 | 0.18 | 42.9 | 0.31 | -6.7 | 5.94 | 122.2 | 388 | 240
TRANSF. 400/225kV 762 QUINTES (LES) | QUINT-Y762 | 400 | 225 | 1660 | 1805 | 0.11 | 42.3 | 0.36 | -6.4 | 5.04 | 124.2 | 388 | 240
TRANSF. 400/225kV 761 REALTOR | REALT-Y761 | 400 | 225 | 1660 | 1805 | 0.12 | 41.7 | 0.34 | -6.6 | 4.95 | 118.8 | 388 | 240
TRANSF. 400/225kV 762 REALTOR | REALT-Y762 | 400 | 225 | 1660 | 1805 | 0.14 | 42.7 | 0.35 | -6.6 | 4.94 | 122.1 | 388 | 240
TRANSF. 400/225kV 763 REALTOR | REALT-Y763 | 400 | 225 | 1660 | 1805 | 0.11 | 41.8 | 0.36 | -6.3 | 4.92 | 120.5 | 388 | 240
TRANSF. 400/225kV 761 REMISE | REMIS-Y761 | 400 | 225 | 829 | 901 | -0.036 | 73.1 | 1.08 | -8.86 | 8.77 | 205.2 | 405 | 240
TRANSF. 400/225kV 764 REVIGNY | REVIG-Y764 | 400 | 225 | 850 | 925 | 0.59 | 69.3 | 0.59 | -10.9 | 2.51 | 220.8 | 380 | 235
TRANSF. 400/225kV 765 REVIGNY | REVIG-Y765 | 400 | 225 | 1659 | 1803 | 0.09 | 42.8 | 0.37 | -6.8 | 4.77 | 121.5 | 388 | 240
TRANSF. 400/225kV 762 ROUGEMONTIER | ROUGE-Y762 | 400 | 225 | 847 | 921 | 0.06 | 71.8 | 0.97 | -8.2 | 7.2 | 289.2 | 380 | 235
TRANSF. 400/225kV 763 ROUGEMONTIER | ROUGE-Y763 | 400 | 225 | 1659 | 1803 | 0.41 | 44.8 | 0.07 | -9 | 2.84 | 120.8 | 388 | 240
TRANSF. 400/225kV 765 ROUGEMONTIER | ROUGE-Y765 | 400 | 225 | 1659 | 1803 | 0.2 | 44.6 | 0.26 | -9.5 | 2.51 | 119 | 388 | 240
TRANSF. 400/225kV 761 RUEYRES | RUEYR-Y761 | 400 | 225 | 829 | 901 | 0.4 | 69.2 | 0.75 | -12 | 4.9 | 211.7 | 380 | 235
TRANSF. 400/225kV 762 RUEYRES | RUEYR-Y762 | 400 | 225 | 840 | 913 | 0.52 | 71.6 | 0.68 | -11.6 | 2.75 | 224.5 | 380 | 235
TRANSF. 400/225kV 761 RULHAT | RULHA-Y761 | 400 | 225 | 847 | 921 | 0.58 | 70.8 | 0.57 | -11 | 2.41 | 221.6 | 380 | 235
TRANSF. 400/225kV 762 RULHAT | RULHA-Y762 | 400 | 225 | 847 | 921 | 0.61 | 67.8 | 0.59 | -10.5 | 5.29 | 210.4 | 380 | 235
TRANSF. 400/225kV 763 RULHAT | RULHA-Y763 | 400 | 225 | 1659 | 1803 | 0.103 | 45.77 | 0.353 | -9.9 | 5.544 | 128.9 | 388 | 240
TRANSF. 400/225kV 761 SAUCATS | SAUCA-Y761 | 400 | 225 | 1659 | 1803 | 0.26 | 45.1 | 0.22 | -9 | 2.53 | 122.2 | 388 | 240
TRANSF. 400/225kV 762 SAUCATS | SAUCA-Y762 | 400 | 225 | 1660 | 1805 | 0.13 | 42.2 | 0.35 | -6.4 | 4.94 | 120.4 | 388 | 240
TRANSF. 400/225kV 763 SAUCATS | SAUCA-Y763 | 400 | 225 | 1659 | 1803 | 0.167 | 40.43 | 0.176 | -5.26 | 4.35 | 130 | 388 | 240
TRANSF. 400/225kV 761 SAUSSET | SAUS5-Y761 | 400 | 225 | 1659 | 1803 | 0.27 | 43 | 0.17 | -6.9 | 2.39 | 121.7 | 388 | 240
TRANSF. 400/225kV 762 SAUSSET | SAUS5-Y762 | 400 | 225 | 1659 | 1803 | 0.09 | 45.9 | 0.41 | -10 | 5.62 | 129.3 | 388 | 240
TRANSF. 400/225kV 761 SCHEER | SCHEE-Y761 | 400 | 225 | 1659 | 1803 | 0.118 | 39.27 | 0.226 | -3.7 | 4.342 | 131 | 388 | 240
TRANSF. 400/225kV 761 SEREIN | SEREI-Y761 | 400 | 225 | 1659 | 1803 | 0.09 | 42.7 | 0.4 | -6.7 | 4.95 | 122.1 | 388 | 240
TRANSF. 400/225kV 762 SEREIN | SEREI-Y762 | 400 | 225 | 1659 | 1803 | 0.12 | 42.7 | 0.37 | -6.7 | 5.21 | 125.4 | 388 | 240
TRANSF. 400/225kV 762 SIERENTZ | SIERE-Y762 | 400 | 225 | 840 | 913 | 0.56 | 69.9 | 1.14 | -12.9 | 5.25 | 211.9 | 380 | 235
TRANSF. 400/225kV 763 SIERENTZ | SIERE-Y763 | 400 | 225 | 840 | 913 | 0.29 | 69.8 | 0.72 | -7.1 | 7.16 | 302.4 | 380 | 235
TRANSF. 400/225kV 764 SIERENTZ | SIERE-Y764 | 400 | 225 | 840 | 913 | 0.62 | 69.9 | 0.51 | -12.7 | 5.41 | 208.3 | 380 | 235
TRANSF. 400/225kV 761 ST-AVOLD | SSAVO-Y761 | 400 | 225 | 1659 | 1803 | 0.13 | 42.6 | 0.29 | -6.8 | 4.6 | 124.6 | 388 | 240
TRANSF. 400/225kV 765 ST-ELOI | SSELO-Y765 | 400 | 225 | 810 | 847 | 0.35 | 68.5 | 0.66 | -7.5 | 6.95 | 307.5 | 380 | 235
TRANSF. 400/225kV 766 ST-ELOI | SSELO-Y766 | 400 | 225 | 810 | 847 | 0.07 | 68.3 | 1.08 | -5.6 | 7.28 | 298.6 | 380 | 235
TRANSF. 400/225kV 761 TABARDERIE | TABAR-Y761 | 400 | 225 | 839 | 912 | 0.66 | 71 | 0.47 | -13.4 | 5.39 | 209 | 380 | 235
TRANSF. 400/225kV 762 TABARDERIE | TABAR-Y762 | 400 | 225 | 839 | 912 | 0.64 | 70.6 | 0.48 | -12.8 | 5.34 | 213 | 380 | 235
TRANSF. 400/225kV 761 TAMAREAU | TAMAR-Y761 | 400 | 225 | 1659 | 1803 | 0.25 | 45 | 0.23 | -8.7 | 2.64 | 120.3 | 388 | 240
TRANSF. 400/225kV 762 TAMAREAU | TAMAR-Y762 | 400 | 225 | 1659 | 1803 | 0.13 | 42.4 | 0.33 | -6.6 | 5.05 | 124.5 | 388 | 240
TRANSF. 400/225kV 763 TAMAREAU | TAMAR-Y763 | 400 | 225 | 1659 | 1803 | 0.02 | 42.5 | 0.45 | -6.6 | 4.84 | 122.4 | 388 | 240
TRANSF. 400/225kV 763 TAVEL | TAVEL-Y763 | 400 | 225 | 1660 | 1805 | 0.14 | 42.6 | 0.33 | -6.6 | 4.97 | 124.9 | 388 | 240
TRANSF. 400/225kV 764 TAVEL | TAVEL-Y764 | 400 | 225 | 1660 | 1805 | 0.15 | 42.5 | 0.32 | -6.5 | 5 | 125 | 388 | 240
TRANSF. 400/225kV 761 TERRIER | TERRI-Y761 | 400 | 225 | 1655 | 1800 | 0.02 | 42.4 | 0.44 | -6.5 | 5.01 | 124.8 | 388 | 240
TRANSF. 400/225kV 762 TERRIER | TERRI-Y762 | 400 | 225 | 1655 | 1800 | 0.31 | 45.6 | 0.18 | -9.3 | 2.53 | 119.8 | 388 | 240
TRANSF. 400/225kV 763 TOURBE | TOURB-Y763 | 400 | 225 | 1661 | 1806 | 0.24 | 46.2 | 0.26 | -9 | 2.63 | 123.2 | 388 | 240
TRANSF. 400/225kV 764 TOURBE | TOURB-Y764 | 400 | 225 | 1661 | 1806 | 0.29 | 45.5 | 0.18 | -9.2 | 2.52 | 122.2 | 388 | 240
TRANSF. 400/225kV 761 TRANS | TRANS-Y761 | 400 | 225 | 1560 | 1803 | 0.09 | 45.9 | 0.37 | -10 | 5.44 | 129.6 | 388 | 240
TRANSF. 400/225kV 762 TRANS | TRANS-Y762 | 400 | 225 | 1659 | 1803 | 0.11 | 45.6 | 0.35 | -9.6 | 5.22 | 129 | 388 | 240
TRANSF. 400/225kV 761 TRICASTIN-POSTE (LE) | TRI.P-Y761 | 400 | 225 | 2654 | 2654 | 0.1 | 50.9 | 0.2 | -31 | 1.4 | 57 | 395 | 230
TRANSF. 400/225kV 762 TRICASTIN-POSTE (LE) | TRI.P-Y762 | 400 | 225 | 2654 | 2654 | 0.1 | 50.9 | 0.2 | -31 | 1.4 | 57 | 395 | 230
TRANSF. 400/225kV 765 TRICASTIN-POSTE (LE) | TRI.P-Y765 | 400 | 225 | 2654 | 2654 | 0.1 | 50.9 | 0.2 | -31 | 1.4 | 57 | 395 | 230
TRANSF. 400/225kV 766 TRICASTIN-POSTE (LE) | TRI.P-Y766 | 400 | 225 | 2654 | 2654 | 0.1 | 50.9 | 0.2 | -31 | 1.4 | 57 | 395 | 230
TRANSF. 400/225kV 761 VALDIVIENNE | VALDI-Y761 | 400 | 225 | 847 | 921 | 0.02 | 68.1 | 1.01 | -5.7 | 6.09 | 296 | 390 | 235
TRANSF. 400/225kV 762 VALDIVIENNE | VALDI-Y762 | 400 | 225 | 847 | 921 | 0.17 | 69.2 | 0.82 | -6.6 | 5.7 | 303 | 380 | 235
TRANSF. 400/225kV 762 VAUPALIERE (LA) | VAUPA-Y762 | 400 | 225 | 1659 | 1803 | 0.32 | 45.2 | 0.17 | -9.3 | 2.55 | 119.9 | 388 | 240
TRANSF. 400/225kV 763 VAUPALIERE (LA) | VAUPA-Y763 | 400 | 225 | 1659 | 1803 | 0.32 | 45.1 | 0.25 | -8.9 | 2.53 | 119.1 | 388 | 240
TRANSF. 400/225kV 764 VAUPALIERE (LA) | VAUPA-Y764 | 400 | 225 | 1659 | 1803 | 0.12 | 42.8 | 0.35 | -6.7 | 4.93 | 122.3 | 388 | 240
TRANSF. 400/225kV 761 VERFEIL | VERFE-Y761 | 400 | 225 | 1660 | 1805 | 0.14 | 42.6 | 0.34 | -6.8 | 4.94 | 121.1 | 388 | 240
TRANSF. 400/225kV 762 VERFEIL | VERFE-Y762 | 400 | 225 | 1660 | 1805 | 0.14 | 42.1 | 0.33 | -6.3 | 4.91 | 122.1 | 388 | 240
TRANSF. 400/225kV 762 VESLE | VESLE-Y762 | 400 | 225 | 1659 | 1803 | 0.16 | 42.9 | 0.32 | -6.7 | 4.73 | 123.8 | 388 | 240
TRANSF. 400/225kV 763 VESLE | VESLE-Y763 | 400 | 225 | 1659 | 1803 | 0.14 | 43.3 | 0.32 | -7.2 | 5.12 | 123.1 | 388 | 240
TRANSF. 400/225kV 761 VIELMOULIN | VIELM-Y761 | 400 | 225 | 839 | 912 | 0.7 | 68.7 | 0.46 | -11.9 | 5.07 | 209.1 | 380 | 235
TRANSF. 400/225kV 762 VIELMOULIN | VIELM-Y762 | 400 | 225 | 1659 | 1803 | 0.25 | 45.2 | 0.22 | -9.1 | 2.51 | 123.1 | 388 | 240
TRANSF. 400/225kV 763 VIELMOULIN | VIELM-Y763 | 400 | 225 | 839 | 912 | 0.5 | 69.4 | 0.65 | -12.7 | 5.44 | 213.2 | 380 | 235
TRANSF. 400/225kV 761 VIGY | VIGY -Y761 | 400 | 225 | 1659 | 1803 | 0.15 | 42.7 | 0.29 | -6.8 | 4.94 | 122.4 | 388 | 240
TRANSF. 400/225kV 763 VIGY | VIGY -Y763 | 400 | 225 | 1659 | 1803 | 0.13 | 42.8 | 0.34 | -6.8 | 4.92 | 122.3 | 388 | 240
TRANSF. 400/225kV 765 VINCEY | VINCE-Y765 | 400 | 225 | 1659 | 1803 | 0.09 | 42.4 | 0.37 | -6.6 | 4.98 | 124.3 | 388 | 240
TRANSF. 400/225kV 766 VINCEY | VINCE-Y766 | 400 | 225 | 1659 | 1803 | 0.29 | 45.2 | 0.18 | -9.1 | 2.46 | 119.4 | 388 | 240
TRANSF. 400/225kV 761 VILLEJUST | VLEJU-Y761 | 400 | 225 | 1659 | 1803 | 0.08 | 42.4 | 0.39 | -6.4 | 4.98 | 121.8 | 388 | 240
TRANSF. 400/225kV 762 VILLEJUST | VLEJU-Y762 | 400 | 225 | 1659 | 1803 | 0.1 | 42.4 | 0.36 | -6.5 | 4.92 | 124.2 | 388 | 240
TRANSF. 400/225kV 763 VILLEJUST | VLEJU-Y763 | 400 | 225 | 1659 | 1803 | 0.29 | 45.5 | 0.18 | -9.2 | 2.72 | 122.9 | 388 | 240
TRANSF. 400/225kV 764 VILLEJUST | VLEJU-Y764 | 400 | 225 | 1659 | 1803 | 0.24 | 45.4 | 0.25 | -9.6 | 2.55 | 120.7 | 388 | 240
TRANSF. 400/225kV 765 VILLEJUST | VLEJU-Y765 | 400 | 225 | 1659 | 1803 | 0.3 | 46 | 0.19 | -9 | 2.63 | 120.6 | 388 | 240
TRANSF. 400/225kV 766 VILLEJUST | VLEJU-Y766 | 400 | 225 | 1659 | 1803 | 0.094 | 39.2 | 0.24 | -3.8 | 4.47 | 131.6 | 388 | 240
TRANSF. 400/225kV 762 VILLEVAUDE | VLEVA-Y762 | 400 | 225 | 1659 | 1803 | 0.27 | 45.8 | 0.21 | -9.3 | 2.62 | 123.9 | 388 | 240
TRANSF. 400/225kV 763 VILLEVAUDE | VLEVA-Y763 | 400 | 225 | 1660 | 1805 | 0.1 | 42.5 | 0.36 | -6.8 | 4.9 | 124.2 | 388 | 240
TRANSF. 400/225kV 764 VILLEVAUDE | VLEVA-Y764 | 400 | 225 | 1660 | 1805 | 0.04 | 42.3 | 0.42 | -6.5 | 4 | 124.9 | 388 | 240
TRANSF. 400/225kV 765 (769) VILLEVAUDE | VLEVA-Y765 | 400 | 225 | 1695 | 1842 | 0.24 | 72 | 0.76 | -9.1 | 7.15 | 307.2 | 380 | 235
TRANSF. 400/225kV 769 VILLEVAUDE | VLEVA-Y769 | 400 | 225 | 847 | 921 | 0.34 | 68.1 | 0.68 | -5.4 | 7.02 | 295.7 | 380 | 235
TRANSF. 400/225kV 761 WARANDE | WARAN-Y761 | 400 | 225 | 1659 | 1803 | 0.28 | 44.8 | 0.22 | -9.3 | 2.62 | 120.9 | 388 | 240
TRANSF. 400/225kV 762 WARANDE | WARAN-Y762 | 400 | 225 | 1659 | 1803 | 0.26 | 45.2 | 0.21 | -9.8 | 2.58 | 119.5 | 388 | 240
TRANSF. 400/225kV 763 WARANDE | WARAN-Y763 | 400 | 225 | 1659 | 1803 | 0.33 | 44.3 | 0.16 | -9 | 2.61 | 120 | 388 | 240
TRANSF. 400/225kV 764 WARANDE | WARAN-Y764 | 400 | 225 | 1659 | 1803 | 0.2 | 44.9 | 0.28 | -8.7 | 2.51 | 120.6 | 388 | 240
TRANSF. 400/225kV 761 WEPPES | WEPPE-Y761 | 400 | 225 | 1659 | 1803 | 0.31 | 46.4 | 0.19 | -9.8 | 2.69 | 119.9 | 388 | 240
TRANSF. 400/225kV 762 WEPPES | WEPPE-Y762 | 400 | 225 | 1659 | 1803 | 0.27 | 45.7 | 0.21 | -9.3 | 2.61 | 121.3 | 388 | 240
TRANSF. 400/225kV 761 YVELINES-OUEST | YVE.O-Y761 | 400 | 225 | 1659 | 1803 | 0.112 | 43.1 | 0.36 | -6.9 | 4.98 | 124.1 | 388 | 240